Application No:       A.08-02-001			
Exhibit No.:				
Witness:	   	   Herbert S. Emmrich

| In the Matter of the Application of San Diego Gas & Electric Company (U 902 G) and Southern California Gas Company (U 904 G) for Authority to Revise Their Rates Effective January 1, 2009, in Their Biennial Cost Allocation Proceeding. | ) ) ) ) ) ) ) | A.08-2-001 (Filed February 4, 2008) |
| --- | --- | --- |

PREPARED DIRECT TESTIMONY

OF HERBERT S. EMMRICH

SAN DIEGO GAS & ELECTRIC COMPANY

AND

SOUTHERN CALIFORNIA GAS COMPANY

DEMAND FORECASTS AND RELATED ISSUES

PHASE II

BEFORE THE PUBLIC UTILITIES COMMISSION
OF THE STATE OF CALIFORNIA

April 24, 2008

TABLE OF CONTENTS

P

Page

I.	QUALIFICATIONS	2

II.	PURPOSE	2

III.	SOCALGAS’ GAS DEMAND FORECASTS (2009 – 2011)	2

A.	Introduction	2

B.	Economics and Customer Growth	2

C.	Gas Demand	2

D.	SoCalGas’ Customer Segment Demand	2

1.      Residential……………………………………………………………….	2

2.	Commercial………………………………………………………….......	2

3.	Industrial………………………………………………………………...	2

4.	Electric Power Generation………………………………………………	2

5.	Enhanced Oil Recovery—Cogeneration and Steaming…………………	2

6.	ECOGAS (Mexicali)…………………………………………………….	2

7.	Wholesale………………………………………………………………..	2

8.	Natural Gas Vehicles……………………………………………………	2

9.	Exchange Gas……………………………………………………………	2

E.	Temperature Sensitivity (SoCalGas)	2

F.	SoCalGas’ Retail Core Peak Day and Peak Month Demand	2

G.	Gas Price Forecast	2

H.	Unaccounted-For (UAF) Gas	2

IV.	SDG&E’S GAS DEMAND FORECASTS (2009 – 2011)	2

A.	Introduction	2

B.	Economics and Customer Growth	2

C.	SDG&E Gas Demand	2

1.	Residential……………………………………………………………….	2

2.	Commercial and Industrial………………………………………………	2

3.	Natural Gas Vehicles……………………………………………………	2

4.	Electric Power Generation………………………………………………	2

D.	Temperature Sensitivity (SDG&E)	2

E.	SDG&E’s Core Peak Day and Peak Month	2

V.	COMBINED SOCALGAS & SDG&E GAS FORECASTS	2

A.	Combined Peak Day Forecasts	2

1.	Combined Core Peak Day Demand Forecasts…………………………..	2

2.	Core Peak Day Storage: Flowing Supply & Withdrawal Capacities……	2

3.	Combined 1-in-10-Annual Likelihood Peak Day Forecasts…………….	2

B.	Combined Annual Throughput Forecasts	2

C.	Combined Long-Term Forecasts	2

PREPARED DIRECT TESTIMONY

OF HERBERT S. EMMRICH

# I.	QUALIFICATIONS

My name is Herbert S. Emmrich.  My business address is 555 West Fifth Street, Los Angeles, California 90013-1011.  I am employed by Southern California Gas Company (SoCalGas) as Gas Demand Forecasting Manager in the Regulatory Affairs Department.  I am responsible for the development of natural gas demand forecasts for San Diego Gas & Electric Company (SDG&E) and SoCalGas.  I have been in this position since March 2004.  I have previously testified before the California Public Utilities Commission (“Commission”).

My academic and professional qualifications are as follows:  I earned an undergraduate degree in Economics and Behavioral Sciences from California State University at Dominguez Hills in 1970 and a Master of Arts Degree in Economics from California State University at Long Beach in 1974.  In addition, during the past 21 years, I held analyst, manager and director level positions in the Regulatory Affairs, Planning, Customer Services, Marketing, Gas Supply and Commercial and Industrial Services Departments of SoCalGas:

- Demand Forecasting and Economic Analysis Manager, Regulatory Affairs Department (March 2004 – Present);

- Regulatory Strategy Manager, Regulatory Affairs Department (2003 –2004);

- Principal Regulatory Policy Analyst, Regulatory Affairs Department (2002 – 2003);

- Director of Special Projects, Commercial and Industrial Services Department (1997 - 1998);

- Director of Sales and Gas Supply Forecasting, Commercial and Industrial Services Department, (1995 - 1997);

- Project Manager, Gas Supply Department (1994 - 1995);

- Gas Supply Planning and Forecasting Manager, Gas Supply Department (1993 - 1994);

- Gas Demand Forecast Manager, Marketing Department (1991 – 1993);

- Project Manager, Customer Services Department, Southern California Gas Company (1990 - 1991);

- Senior Analyst, Strategic Planning Department (1984 - 1990).

My employment outside of SoCalGas has been in the areas of economics, environmental assessment, and business planning and energy sector development.  I held the positions of: Economist, Regional Economist and Environmental Assessment Manager at the U.S. Bureau of Land Management’s Pacific Outer Continental Shelf Office, in Los Angeles, from 1975 to 1979; Economic Policy Supervisor and Issues and Policy Manager of Getty Oil Company from 1979 to 1984; and, Senior Energy Advisor of the U.S. Agency for International Development’s Caucasus Office in Tbilisi, Republic of Georgia, from 1998 to 2002.

# II.	PURPOSE

The purpose of my testimony is to present the average temperature year, cold temperature year and extreme design peak day gas demand forecasts for the years 2009 through 2011 for SDG&E and SoCalGas’ residential, core commercial and industrial, non-core commercial and industrial, enhanced oil recovery (EOR), natural gas vehicle (NGV), wholesale customer classes, and ECOGAS in Mexicali, Mexico. The details of the electric generation (EG) and cogeneration forecasts of gas demand are shown in the prepared direct testimony of Mr. Anderson.  My testimony also presents the gas prices used to forecast demand by customer segment.  My testimony presents SDG&E and SoCalGas’ unaccounted-for (UAF) gas and company-use fuel requirements and their allocation to the core and non-core customer classes.  
III.	SOCALGAS’ GAS DEMAND FORECASTS (2009 – 2011)

## A.	Introduction

SoCalGas is the principal distributor of natural gas in southern California, providing retail and wholesale customers with procurement, transportation, and storage services.  In addition to serving the residential, commercial, and industrial markets, SoCalGas provides gas for the EOR and EG markets in southern California.  SDG&E, Southwest Gas Corporation (SWG), the City of Vernon (Vernon), and the City of Long Beach Gas and Oil Department (Long Beach) are SoCalGas’ four wholesale customers. SoCalGas also provides gas service to ECOGAS in Mexicali, Mexico.  The forecast begins with a discussion of the economic conditions facing the utilities, followed by a discussion of the factors affecting gas demand in various market sectors.  Summary tables and figures underlying the forecast are provided.

## B.	Economics and Customer Growth

From 2006 through 2011, SoCalGas service-area non-farm jobs should see nearly 1.1% average annual growth.  Area industrial jobs should remain essentially flat during this period, and we expect the industrial share of non-farm employment to fall from 11.1% to 10.3%.  Commercial jobs should average 1.2% annual growth from 2006 through 2011.  Mainly as a result of growing numbers of residents, we expect SoCalGas’ total active meters to increase an average of about 1.3% per year from 5.392 million in 2006 to 5.745 million in 2011.  Table 1 details SoCalGas’ expected meter counts during the 2009 to 2011 BCAP period.

Table 1

SoCalGas Active Meters (annual averages)

|  |  | 2009 | 2010 | 2011 | 2-Year Avg. 2009-2010 | 3-Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- | --- |
| Core |  |  |  |  |  |  |
|  | Residential | 5,383,344 | 5,455,319 | 5,527,388 | 5,419,331 | 5,455,350 |
|  | Core C&I | 214,540 | 215,333 | 215,986 | 214,936 | 215,286 |
|  | Gas AC | 16 | 16 | 15 | 16 | 16 |
|  | Gas Engine | 850 | 845 | 840 | 848 | 845 |
|  | NGV | 257 | 273 | 289 | 265 | 273 |
|  | Total Core | 5,599,007 | 5,671,785 | 5,744,517 | 5,635,396 | 5,671,770 |
| Non-Core |  |  |  |  |  |  |
|  | Non-core C&I | 706 | 705 | 705 | 706 | 705 |
|  | Electric Generation | 226 | 219 | 213 | 223 | 219 |
|  | EOR | 32 | 32 | 32 | 32 | 32 |
|  | Total Retail Non-core | 964 | 956 | 950 | 960 | 957 |
| Wholesale and International |  | 5 | 5 | 5 | 5 | 5 |
| System Total Active Meters |  | 5,599,976 | 5,672,746 | 5,745,472 | 5,636,361 | 5,672,732 |

SoCalGas uses econometric and statistical techniques to develop forecasts of residential single family, residential multi-family, commercial and industrial meters. Major economic and demographic assumptions underlying the meter forecast are from Global Insight’s Spring 2007 Regional forecast (state-level and the six most populous counties in SoCalGas’ service territory) released in May 2007.

Connected residential single-family and multi-family meters are a function of lagged authorized housing permits.  A small third sector of the residential class --master meters (including sub-metered customers) -- is forecasted to decline at a steady 0.8% annual rate.  Connected meters in the industrial and commercial sectors are forecasted based on lagged employment in those corresponding sectors.

Once the number of connected meters is forecasted for each customer class, it is split into active and inactive meters, where inactive meters are those with no billed gas use during a billing period.  Inactive meters are forecasted by applying a factor to each customer class of forecasted connected meters. The factors used are based on seasonal and multi-year historical patterns of inactive meters for that particular customer class.  The number of active meters is equal to the number of connected meters less the number of inactive meters.

Both the core commercial and core industrial active meters are forecasted based on recent historical ratios of those core active meters to their total active commercial and industrial meters, respectively.  For gas air conditioning (GAC), we expect 16 meters for years 2009 and 2010 and 15 for year 2011. The number of gas engine meters is expected to decline from 878 in 2006 to 840 in 2011.

## C.	Gas Demand

We expect continued gas demand growth in the residential market, as well as in associated service-oriented businesses in the commercial market.  These markets, along with small- and medium-sized industrial customers, comprise the core market.  The remaining large customers make up the non-core market.  There has been some movement between the two markets. Since the last BCAP in 1999, through 2007, a net number of 337 customers shifted from the non-core to the core market; in 2007 this resulted in a net throughput shift of 3,214 MDth from the non-core to the core market.

Table 2 shows the composition of SoCalGas’ throughput forecast for 2009, 2010 and 2011 under Average Temperature Year conditions and Table 3 shows demand under Cold Year Temperature conditions.

Table 2

Composition of SoCalGas Throughput (MDth) Average Temperature Year

|  |  | 2009 | 2010 | 2011 | 2-Year Avg. 2009-2010 | 3-Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- | --- |
| Core |  |  |  |  |  |  |
|  | Residential | 247,209 | 248,403 | 249,585 | 247,806 | 248,399 |
|  | Core C&I | 98,245 | 97,129 | 95,782 | 97,687 | 97,052 |
|  | Gas AC | 124 | 124 | 116 | 124 | 121 |
|  | Gas Engine | 1,819 | 1,808 | 1,797 | 1,813 | 1,808 |
|  | NGV | 10,332 | 11,666 | 13,172 | 10,999 | 11,723 |
|  | Total Core | 357,727 | 359,129 | 360,453 | 358,428 | 359,103 |
| Non-Core |  |  |  |  |  |  |
|  | Non-core C&I | 143,918 | 144,034 | 144,097 | 143,976 | 144,016 |
|  | Electric Generation | 283,888 | 280,328 | 283,873 | 282,108 | 282,696 |
|  | EOR | 17,684 | 14,586 | 14,586 | 16,135 | 15,619 |
|  | Total Retail Non-core | 445,490 | 438,948 | 442,556 | 442,219 | 442,331 |
| Wholesale and International |  |  |  |  |  |  |
|  | Long Beach | 11,730 | 11,684 | 11,715 | 11,707 | 11,709 |
|  | SDG&E | 125,323 | 127,180 | 116,583 | 126,251 | 123,029 |
|  | Southwest Gas | 7,951 | 8,174 | 8,396 | 8,063 | 8,174 |
|  | Vernon | 11,500 | 11,622 | 11,718 | 11,561 | 11,613 |
|  | Mexicali | 5,366 | 5,414 | 5,417 | 5,390 | 5,399 |
|  | Total Wholesale & Intl. | 161,869 | 164,074 | 153,828 | 162,972 | 159,924 |
| Average Year Throughput |  | 965,086 | 962,151 | 956,836 | 963,619 | 961,358 |

Table 3

Composition of SoCalGas Throughput (MDth) 1-in-35 Cold Temperature Year

|  |  | 2009 | 2010 | 2011 | 2-Year Avg. 2009-2010 | 3-Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- | --- |
| Core |  |  |  |  |  |  |
|  | Residential | 271,041 | 272,350 | 273,646 | 271,695 | 272,346 |
|  | Core C&I | 103,027 | 101,858 | 100,446 | 102,442 | 101,777 |
|  | Gas AC | 124 | 124 | 116 | 124 | 121 |
|  | Gas Engine | 1,819 | 1,808 | 1,797 | 1,813 | 1,808 |
|  | NGV | 10,332 | 11,666 | 13,172 | 10,999 | 11,723 |
|  | Total Core | 386,342 | 387,805 | 389,178 | 387,073 | 387,775 |
| Non-Core |  |  |  |  |  |  |
|  | Non-core C&I | 144,375 | 144,491 | 144,553 | 144,433 | 144,473 |
|  | Electric Generation | 283,888 | 280,328 | 283,873 | 282,108 | 282,696 |
|  | EOR | 17,684 | 14,586 | 14,586 | 16,135 | 15,619 |
|  | Total Retail Non-core | 445,946 | 439,405 | 443,013 | 442,676 | 442,788 |
| Wholesale and International |  |  |  |  |  |  |
|  | Long Beach | 12,385 | 12,339 | 12,370 | 12,362 | 12,364 |
|  | SDG&E | 130,649 | 132,532 | 121,950 | 131,590 | 128,377 |
|  | Southwest Gas | 8,149 | 8,380 | 8,610 | 8,264 | 8,380 |
|  | Vernon | 11,500 | 11,622 | 11,718 | 11,561 | 11,613 |
|  | Mexicali | 5,366 | 5,414 | 5,417 | 5,390 | 5,399 |
|  | Total Wholesale & Intl. | 168,048 | 170,286 | 160,065 | 169,167 | 166,133 |
| Cold Year Throughput |  | 1,000,336 | 997,496 | 992,255 | 998,916 | 996,696 |

## D.	SoCalGas’ Customer Segment Demand

### 1.	Residential

Active residential meters averaged 5.18 million in 2006, an increase of about 1.3% from the 2005 average.  From 2009 through 2011, SoCalGas’ active residential customer base is expected to grow at an average annual rate of 1.3%, reaching nearly 5.53 million by 2011.

Residential gas demand adjusted for temperature decreased to 250,616 MDth in 2006 from 259,267 MDth in 2005.  Temperature-adjusted residential demand is projected to grow from 247,209 MDth in 2009 to 249,585 MDth in 2011, an increase of about 2,376 MDth or 0.5% per year.  This forecast reflects the savings from SoCalGas’ energy efficiency programs, which are described in Commission Decision 04-09-060, and in SoCalGas’ Advice Letter 3588 of February 1, 2006.

### 2.	Commercial

On a temperature-adjusted basis, core commercial market demand in 2006 totaled 79,429 MDth, up 409 MDth from the 2005 commercial load totaling 79,020 MDth.  This increase is largely the result of economic growth in southern California.  Over the BCAP period, core commercial market demand is forecasted to decrease about 1.2% per year dropping from 76,832 MDth in 2009 to 75,059 MDth by 2011.  This decrease is due to Commission-mandated energy efficiency savings programs.

During the BCAP period from 2009 to 2011, non-core commercial demand is forecasted to average nearly 22,500 MDth per year, slightly higher than 2006 actual usage of 22,400 MDth.  Most of the increasing demand from the lodging, health, office buildings and agricultural sectors is being offset by decreased demand in the construction sector. The net gain of 1.2% from economic growth is expected to be reduced by a loss of -0.7% from mandated demand-side management (DSM) savings, and by the departure in 2008 of two customers to the City of Vernon (a wholesale customer).

Table 4

Average Year Commercial Demand Forecast in MDth

|  | 2009 | 2010 | 2011 | 2 Year Avg. 2009-2010 | 3 Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- |
| Core Commercial | 76,832 | 76,046 | 75,059 | 76,439 | 75,979 |
| Non-core Commercial | 22,367 | 22,491 | 22,588 | 22,429 | 22,482 |
| Total | 99,199 | 98,537 | 97,647 | 98,868 | 98,461 |

### 3.	Industrial

In 2006, temperature-adjusted core industrial demand was 23,926 MDth, an increase of 76 MDth (0.3%) over 2005 deliveries.  Core industrial market demand is projected to decrease by 2.8% per year from 2006 to 20,723 MDth in 2011.  This demand decrease stems mainly from Commission-mandated energy efficiency savings for the years 2006 through 2011.

Retail non-core industrial demand grew from 62,600 MDth in 2005 to 63,200 MDth in 2006 due to increased activities in the food processing and petroleum sectors. However, this growth is not sustained in the BCAP period from 2009 through 2011, and annual gas demand for this market is expected to drop below 58,000 MDth -- an 8% drop from the 2006 level. Twenty-two percent of this drop is caused by an overall decrease in manufacturing activities, especially the textile and primary metal manufacturing sectors. Seventy-three percent of this drop is caused by the 2008 departure of more than two dozen large industrial customers to the City of Vernon (a wholesale customer), and the other 5% of the drop by caused by Commission-mandated energy efficiency savings during the BCAP period.

Refinery industrial demand is comprised of gas consumption by petroleum refining customers, hydrogen producers and petroleum refined product transporters.  Refinery industrial demand is forecasted separately from other industrial demand due to the complex nature of these customers.  These customers are characterized by a complex interaction of refinery operations, on-site production of alternate fuels, and changing regulatory requirements impacting the production of petroleum products.  Refinery industrial demand is forecasted to be stable at nearly 64,000 MDth per year for calendar years 2009 through 2011.  This is 3,000 MDth lower than the 67,000 MDth recorded in 2006. This decrease is mainly due to the refineries’ use of alternate fuels such as butane during summer months where natural gas prices are forecasted to be less competitive than the alternate fuel prices.  The reduction of refinery gas demand also reflects savings from both Commission-mandated energy efficiency programs and other refinery process-related energy-efficient improvements that are ineligible for SoCalGas’ energy efficiency programs.

Table 5

Average Year Industrial Demand Forecast in MDth

|  | 2009 | 2010 | 2011 | 2 Year Avg. 2009-2010 | 3 Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- |
| Core Industrial | 21,412 | 21,083 | 20,723 | 21,247 | 21,073 |
| Non-core Industrial | 57,819 | 57,872 | 57,920 | 57,845 | 57,870 |
| Industrial Refinery | 63,732 | 63,671 | 63,588 | 63,701 | 63,664 |
| Total | 142,963 | 142,626 | 142,231 | 142,794 | 142,607 |

### 4.	Electric Power Generation

This sector includes the markets for all industrial/commercial cogeneration, and non-cogeneration EG.  Small Industrial/Commercial and refinery cogeneration demand is included in this testimony; the other sectors of electric power generation demand are sponsored by Mr. Anderson and are discussed in his prepared direct testimony.

#### (a)	Industrial/Commercial Cogeneration <20 Megawatts (MW)

Most of the cogeneration units in this non-core segment are installed mainly to generate electricity for customers’ internal consumption rather than for power sales to electric utilities.  In  2006, gas deliveries to this market were 18,093 MDth, down almost 1,700 MDth from 2005’s deliveries of 19,786 MDth.  Small Industrial/Commercial cogeneration demand is projected to average 18,668 MDth per year during the BCAP period.  The forecast includes an anticipated downward adjustment due to a change in eligibility requirements which will cause some of the non-core cogeneration customers to switch to core service starting in late 2009.

#### (b)	Refinery Cogeneration

Refinery cogeneration units are installed primarily to generate electricity for internal use.  Refinery-related cogeneration is forecast to remain steady at 18,200 MDth for the 2009 to 2011 BCAP period.  This is almost the same as the year 2006 recorded throughput.

### 5.	Enhanced Oil Recovery—Cogeneration and Steaming

The EOR demand forecast is prepared based on historical throughput, knowledge of customer operations, and general market conditions.  For the 2009 to 2011 BCAP period, SoCalGas forecasts EOR–related cogeneration usage to average 4,900 MDth per year.  This is a decrease from the 2006 recorded gas deliveries of 18,100 MDth.  This decrease is mainly due to forecasted increased bypass to the Kern River/Mojave Interstate Pipeline (Kern/Mojave) as EOR long-term gas transportation contracts (LTKs) with SoCalGas expire.  Because most of the EOR producers are already connected directly to Kern/Mojave or own laterals in close proximity to facilities that are not currently connected, it is unlikely that SoCalGas will be able to retain much, if any, of the load contracted under the LTKs.  The price of intrastate transportation on Kern/Mojave is usually less than SoCalGas’ short-run marginal cost and is expected to continue to be so during the BCAP period.

For the 2009 to 2011 BCAP period, SoCalGas forecasts EOR steaming usage to average 10,700 MDth per year.  This is a decrease from the 2006 recorded gas deliveries of 14,800 MDth.  As explained above, the decrease in this market is mainly due to forecasted increased bypass to Kern/Mojave as EOR LTKs with SoCalGas expire. However, the decrease is partially offset by new load coming on line as a result of the expansion of oil production operations in existing fields that are not already interconnected with -- or are located far away from -- other gas pipelines.

### 6.	ECOGAS (Mexicali)

For this forecast, SoCalGas and SDG&E used the 2006 California Gas Report (CGR) forecast prepared by ECOGAS of Mexicali.  Mexicali’s use is expected to increase from 5,291 MDth in 2006 to 5,417 MDth in 2011.

### 7.	Wholesale

The forecast of wholesale gas demand includes transportation service to SDG&E, Long Beach, Southwest Gas (SWG), and Vernon.

The non-EG gas demand forecast for SDG&E is made on a customer class basis.  Under average temperature conditions, total non-EG requirements for SDG&E are expected to decrease from 54,777 MDth in 2006 to 54,164 MDth in 2011 mainly due to a decrease in the Commercial and Industrial markets from Commission-mandated energy efficiency measures.

The forecast of the non-cogeneration EG loads in SDG&E’s area is based on power market simulation as noted in Mr. Anderson’s testimony on EG demand.  The forecast assumes a decrease in SDG&E’s EG gas requirements from 63,117 MDth in 2006 to 61,981 MDth in 2011.

For Long Beach, the forecast prepared by Long Beach for the 2006 CGR was used.  Long Beach’s usage is expected to remain steady at 12,300 MDth per year, with Long Beach's annual local supply at 600 MDth and SoCalGas’ transportation deliveries to Long Beach at 11,700 MDth per year.

The demand forecast for SWG is based on a demand forecast prepared by Southwest Gas for the 2006 CGR. The direct service load is expected to grow 2.4% per year from 7,460 MDth in 2006 to 8,396 MDth in 2011.

Vernon initiated municipal gas service to its electric power plant in June 2005 and to non-core customers in December 2006.  The forecasted annual usage averages 11,613 MDth for the 2009-2011 BCAP period. Vernon’s commercial and industrial load is based on recorded 2006 usage for commercial and industrial customers already served by Vernon plus those additional customers that are expected to request retail service from Vernon.   The throughput forecast for Vernon EG customers is based on the power market simulation as noted in Mr. Anderson’s testimony on EG demand.

### 8.	Natural Gas Vehicles

NGV throughput is expected to increase from 7,758 MDth in 2006 to 10,332 MDth in 2009 and 13,172 MDth in 2011, with the number of stations rising from 258 in 2009 to 282 in 2011.  SoCalGas remains optimistic about the NGV market, with growth expected in both private and public sectors.  Most of the NGV growth in the public sector is expected to come from public transit, goods movement, and trash haulers. SoCalGas recently introduced a new tariff for home NGV refueling.  There is currently one known home refueling appliance unit on the market in SoCalGas’ service area.  Manufactured by FuelMaker, this unit allows customers to refuel their NGVs at home using their existing residential gas service. This product should boost NGV market growth by providing residential support to the growing NGV station infrastructure.

### 9.	Exchange Gas

The exchange of gas between SoCalGas and PG&E has been in practice since 1949.  With the termination of the General Service Mutual Assistance Agreement between the two companies on May 5, 1988, the Commission ordered the two companies to renegotiate a uniform procedure for exchanging gas.  This instrument is called the Master Exchange Agreement (MEA), which the Commission approved on February 7, 1990.

Table 6.

Exchange Gas Forecast in MDth

|  | 2009 | 2010 | 2011 | 2 year Avg. 2009-2010 | 3 Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- |
| SoCalGas Deliveries to PG&E | 425 | 425 | 425 | 425 | 425 |
| PG&E Deliveries to SoCalGas | 778 | 778 | 778 | 778 | 778 |
| Net Difference | -353 | -353 | -353 | -353 | -353 |

The net exchange of gas deliveries under the MEA is forecasted to be 353 MDth each year over the period 2009-2011.  SoCalGas annual deliveries are expected to equal 425 MDth , while PG&E deliveries are expected to be 778 MDth.  A negative exchange number indicates that PG&E deliveries to SoCalGas exceed SoCalGas deliveries to PG&E during the year.

## E.	Temperature Sensitivity (SoCalGas)

Core demand forecasts are prepared for two design temperature conditions – average and cold – to quantify changes in space heating demand due to weather.  Temperature variations can cause significant changes in winter gas demand due to space heating principally in the residential and commercial markets.  The largest demand variations due to temperature generally occur in the month of December.  Heating-degree-day (HDD) differences between the two design temperature conditions are developed from a six-zone temperature monitoring procedure within SoCalGas’ service territory.  The cold design temperature conditions are based on a criterion that the temperature condition would be exceeded with a one-chance-in-35 annual likelihood and corresponds to 1,665 HDD for a cold design temperature year.  This contrasts to 1,379 HDD for an average design temperature year.  (The average year total is the simple average of the annual calendar-year HDD totals for the 20-year period from 1987 through 2006.  The cold year HDD value is 2.025 standard deviations (standard deviation =141.25 HDD, calculated from the same 20-year annual historical HDD data) more than the average year HDD total.  Assumed monthly HDD values are shown in Table 7.

Table 7

SoCalGas Heating Degree Days Weather Design

|  | Cold |  | Average | Hot |  |
| --- | --- | --- | --- | --- | --- |
|  | 1-in-35 design | 1-in-10 design |  | 1-in-10 design | 1-in-35 design |
| January | 349 | 328 | 289 | 250 | 229 |
| February | 278 | 262 | 230 | 199 | 183 |
| March | 230 | 216 | 190 | 164 | 151 |
| April | 140 | 132 | 116 | 100 | 92 |
| May | 61 | 57 | 50 | 43 | 40 |
| June | 18 | 17 | 15 | 13 | 12 |
| July | 2 | 2 | 2 | 2 | 2 |
| August | 2 | 2 | 1 | 1 | 1 |
| September | 5 | 5 | 4 | 3 | 3 |
| October | 41 | 39 | 34 | 30 | 27 |
| November | 179 | 168 | 148 | 128 | 117 |
| December | 360 | 339 | 298 | 258 | 236 |
|  | 1,665 | 1,567 | 1,379 | 1,191 | 1,093 |

## F.	SoCalGas’ Retail Core Peak Day and Peak Month Demand

SoCalGas plans and designs its system to provide continuous service to its core (retail and wholesale) customers under an extreme peak day event.  The extreme peak day design criteria are defined as a 1-in-35 annual event; this corresponds to a system average temperature of 38.8 degrees Fahrenheit or 26.2 HDD on a peak day.  Core demand on an extreme peak day is met through a combination of withdrawals from underground storage facilities and flowing pipeline supplies.

For peak month planning, December demand is used, since December has generally been the coldest month in SoCalGas’ service territory based on more than 20 years of weather records. Tables 8 and 9 below show the forecasted retail core peak day demand and cold design-temperature-year peak month demand.

Table 8

1-in-35 Annual Likelihood (38.8°F System Avg. Temperature)

Peak Day Core Demand in MDth/day

|  | 2009 | 2010 | 2011 | 2-Year Avg. 2009-2010 | 3-Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- |
| Residential | 2,560 | 2,567 | 2,574 | 2,563 | 2,567 |
| Core C&I | 584 | 577 | 569 | 581 | 577 |
| Gas AC | 0 | 0 | 0 | 0.2 | 0.2 |
| Gas Engine | 3 | 3 | 3 | 3 | 3 |
| NGV | 28 | 32 | 36 | 30 | 32 |
| Total Core Peak Day | 3,175 | 3,179 | 3,182 | 3,177 | 3,179 |

Table 9

Cold Design Temperature Year: Peak Month Demand in MDth

|  | 2009 | 2010 | 2011 | 2-Year Avg. 2009-2010 | 3-Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- |
| Residential | 41,228 | 41,427 | 41,624 | 41,328 | 41,427 |
| Core C&I | 11,532 | 11,383 | 11,228 | 11,457 | 11,381 |
| Gas AC | 7 | 7 | 7 | 7 | 7 |
| Gas Engine | 85 | 85 | 84 | 85 | 85 |
| NGV | 865 | 976 | 1,103 | 921 | 981 |
| Total Core Peak Month | 53,717 | 53,879 | 54,046 | 53,798 | 53,881 |

## G.	Gas Price Forecast

The natural gas price forecast used to develop the demand forecasts for SoCalGas and SDG&E in this proceeding was prepared in June 2007 and is consistent with the Market Price Referent gas price forecast methodology adopted by the Commission in D.05-12-042./  The natural gas price forecast at Henry Hub from 2009 through 2011 is based on the then-most-recent 22-day trading average of NYMEX futures prices from May 1, 2007 to May 31, 2007.  Basis swaps trading contract settlements from NYMEX ClearPort/ are then added to the Henry Hub futures prices to arrive at the price forecasts at producing basins and at the California border.

As a result of the Omnibus decision (D.07-12-019) that combined the gas procurement functions of SoCalGas and SDG&E, a combined core Weighted Average Cost of Gas (WACOG) for both utilities was estimated using last year’s purchase weights by basin from each utility and the associated expected basin prices. The final WACOG for purchase also includes the integrated interstate pipeline demand charge for both utilities from historical total reservation costs.

Table 10

SoCalGas and SDG&E Combined WACOG

|  | Nominal $/MMBtu | Constant 2008$/MMBtu |
| --- | --- | --- |
| 2009 | 8.26 | 8.10 |
| 2010 | 7.97 | 7.65 |
| 2011 | 7.71 | 7.24 |
| Two-Year Average (2009-2010) | 8.12 | 7.88 |
| Three-Year Average (2009-2011) | 7.98 | 7.66 |

## H.	Unaccounted-For (UAF) Gas

UAF gas is comprised of the following major elements: accounting corrections and prior period adjustments; measurement adjustments; leakage; theft; and other unexplained unaccounted-for volumes.

The recorded UAF gas, including adjustments, as percentages of total gas receipts for the years 2004, 2005 and 2006 for SoCalGas and SDG&E are:

Table 11

SoCalGas and SDG&E UAF Annual Percentages

|  | 2004 | 2005 | 2006 | Average |
| --- | --- | --- | --- | --- |
| SoCalGas | 0.97% | 0.93% | 0.73% | 0.88% |
| SDG&E | 0.45% | 0.95% | 1.27% | 0.87% |

At present, SoCalGas and SDG&E each individually have a 1% UAF gas factor in rates. Currently SoCalGas’ UAF gas allocation factor is based on the 1991 UAF gas study, while SDG&E uses an equal-cents-per-therm (ECPT) allocation factor.

The 1991 UAF gas study isolated UAF gas based on: accounting adjustments; the kinds of measurement devices used to account for gas delivered to core or non-core customers; leakage from distribution services and mains and transmission systems; and estimates of theft-related losses.  The UAF gas class allocation factors based on that study and adopted in the SoCalGas 1999 BCAP were: 32% non-core and 68% core. SDG&E’s factors based on the ECPT allocation resulted in a 59% non-core and 41% core allocation for the 2004 to 2006 period.

In 2007, SoCalGas updated the 1991 study for both SoCalGas and SDG&E based on 2006 throughput and found that the customer class allocation factors should be changed to reflect the overall cost of providing service for the core and non-core classes of customers. The updated study shows the following:

Table 12

SoCalGas & SDG&E 2006 UAF Gas Allocation Factors

|  | UAF (MMBtu) | Core Portion | Non-core Portion |
| --- | --- | --- | --- |
| SoCalGas | 7,256,200 | 71% | 29% |
| SDG&E | 1,549,400 | 77% | 23% |

The complete updated UAF gas study is included as Attachment 1 to this testimony.  Based on the updated study results, SoCalGas and SDG&E recommend that the Commission adopt the three-year average UAF factor of 0.88% for SoCalGas and 0.87% for SDG&E.  It is further recommended that 71% of SoCalGas’ UAF be allocated to core customers and 29% to the non-core class, and that 77% of SDG&E’s UAF be allocated to the core class and 23% to non-core customers’ rates.

# IV.	SDG&E’S GAS DEMAND FORECASTS (2009 – 2011)

## A.	Introduction

SDG&E delivers natural gas to over 840,000 customers in San Diego County.  Gas sales and transportation through SDG&E’s system in 2006 totaled 117,894 MDth, which is an average of 323 MDth/day. SDG&E’s forecast report begins with a discussion of area economic conditions, followed by a discussion of the factors affecting gas demand in various market sectors.  Summary tables and figures underlying the forecast are provided.

## B.	Economics and Customer Growth

Non-farm jobs in San Diego County should grow an average of 1.2% per year, rising from 1.29 million in 2006 to 1.37 million by 2011.  The County’s industrial (manufacturing) jobs are expected to remain virtually flat at just over 100,000 through the forecast period, with manufacturing’s share of non-farm employment falling from 8.1% to 7.5%.  Commercial jobs should average 1.35% annual growth from 2006 through 2011.  Mainly as a result of growing numbers of residents in San Diego County, SDG&E’s total number of gas meters is expected to increase an average of about 1.0% per year from 2006 to 2011.  Table 13 details SDG&E’s expected meter counts for the 2009-2011 BCAP period.

Table 13

SDG&E Meters (Annual Averages)

|  |  | 2009 | 2010 | 2011 | 2-Year Avg. 2009-2010 | 3-Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- | --- |
| Core |  |  |  |  |  |  |
|  | Residential | 821,356 | 831,675 | 843,121 | 826,515 | 832,050 |
|  | Core C&I | 29,864 | 29,833 | 29,797 | 29,848 | 29,831 |
|  | NGV | 38 | 40 | 43 | 39 | 40 |
|  | Total Core | 851,258 | 861,548 | 872,961 | 856,403 | 861,922 |
| Non-Core |  |  |  |  |  |  |
|  | Non-core C&I | 61 | 61 | 61 | 61 | 61 |
|  | Electric Generation | 82 | 81 | 81 | 81 | 81 |
|  | Total Retail Non-core | 143 | 142 | 142 | 142 | 142 |
| System Total Meters |  | 851,400 | 861,690 | 873,103 | 856,545 | 862,064 |

SDG&E’s forecasting models were developed using regression models which integrate input assumptions regarding demographics, economics, and measurable factors which affect gas meter growth. Those input assumptions were based on Global Insight’s Spring 2007 Regional forecast (California state-level and for San Diego County) released in May 2007.  The residential meters were modeled as a function of the service area’s expected level of housing starts as well as seasonal factors.  Commercial and industrial meters were modeled as a function of regional employment growth and seasonal patterns.

## C.	SDG&E Gas Demand

The outlook for SDG&E’s gas sales and transportation demand, excluding cogeneration and EG gas demand, is projected to increase by an average of about 0.3% annually from 2009 to 2011. Assumptions for SDG&E’s gas transport requirements for cogeneration and EG are included as part of the wholesale market sector description for southern California.

The forecast presents core and non-core sales, transportation customer gas consumption, and peak demand for the SDG&E service territory, with the exception of gas requirements for the fossil fuel power plants.  Customer gas usage forecasts are derived from models that integrate demographic assumptions, economics, energy prices, conservation, marketing programs, building and appliance standards, weather, and other factors. Tables 14 and 15 show details of SDG&E’s forecasted annual gas demand under average-year and 1-in-35 cold-year conditions.

Table 14

Composition of SDG&E Throughput in MDth Average Temperature Year

|  |  | 2009 | 2010 | 2011 | 2-Year Avg. 2009-2010 | 3-Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- | --- |
| Core |  |  |  |  |  |  |
|  | Residential | 32,351 | 32,612 | 32,837 | 32,482 | 32,600 |
|  | Core C&I | 16,074 | 15,895 | 15,648 | 15,985 | 15,873 |
|  | NGV | 1,343 | 1,516 | 1,712 | 1,430 | 1,524 |
|  | Total Core | 49,769 | 50,024 | 50,197 | 49,896 | 49,997 |
| Non-Core |  |  |  |  |  |  |
|  | Non-core C&I | 4,123 | 4,050 | 3,967 | 4,086 | 4,046 |
|  | Electric Generation | 70,011 | 71,665 | 61,098 | 70,838 | 67,592 |
|  | Total Retail Non-core | 74,134 | 75,715 | 65,065 | 74,925 | 71,638 |
| Average Year Throughput |  | 123,903 | 125,739 | 115,262 | 124,821 | 121,635 |

Table 15

Composition of SDG&E Throughput in MDth 1-in-35 Cold Year Temperature

|  |  | 2009 | 2010 | 2011 | 2-Year Avg. 2009-2010 | 3-Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- | --- |
| Core |  |  |  |  |  |  |
|  | Residential | 36,698 | 36,993 | 37,249 | 36,845 | 36,980 |
|  | Core C&I | 16,994 | 16,805 | 16,543 | 16,900 | 16,781 |
|  | NGV | 1,343 | 1,516 | 1,712 | 1,430 | 1,524 |
|  | Total Core | 55,035 | 55,315 | 55,504 | 55,175 | 55,284 |
| Non-Core |  |  |  |  |  |  |
|  | Non-core C&I | 4,123 | 4,050 | 3,967 | 4,086 | 4,046 |
|  | Electric Generation | 70,011 | 71,665 | 61,098 | 70,838 | 67,592 |
|  | Total Retail Non-core | 74,134 | 75,715 | 65,065 | 74,925 | 71,638 |
| Cold Year Throughput |  | 129,169 | 131,030 | 120,568 | 130,099 | 126,922 |

### 1.	Residential

Residential meters averaged 799,352 meters in 2006, an increase of about 0.6% from the 2005 average. From 2009 through 2011, SDG&E’s residential customer base is expected to grow at an average annual rate of 1.3%, reaching 843,121 meters by 2011.  Residential gas demand adjusted for temperature totaled 31,988 MDth in 2006. Residential demand is projected to grow from 32,351 MDth in 2009 to 32,837 MDth in 2011, an increase of about 0.7% per year.  This forecast reflects the savings from SDG&E’s energy efficiency programs, which are described in Commission Decision 04-09-060, and in SDG&E’s Advice Letter 1591-G of February 1, 2006.

### 2.	Commercial and Industrial

On a temperature-adjusted basis, core commercial market demand in 2006 totaled 14,778 MDth. Core commercial demand is forecasted to decline to 14,305 MDth in 2009 and 13,887 MDth by 2011.  In 2006, SDG&E’s temperature-adjusted core industrial demand was 1,851 MDth. Core industrial market demand is projected to decrease by approximately 0.23% per year to about 1,761 MDth in 2011.  The decrease in the core commercial and industrial demand is caused by the Commission-mandated energy efficiency savings for the years 2006 through 2011.

Retail non-core commercial and industrial demand is expected to drop from 4,123 MDth in 2009 to 3,967 MDth by 2011.

### 3.	Natural Gas Vehicles

SDG&E’s NGV throughput is expected to increase from 1,030 MDth in 2006 to 1,343 MDth in 2009 and 1,712 MDth in 2011, with growth expected in both private and public sectors.

### 4.	Electric Power Generation

Small cogeneration demand is included in this testimony; the other sectors of electric power generation demand are sponsored by Mr. Anderson and are discussed in his prepared direct testimony.

SDG&E currently has about 60 small cogeneration customers. This load was 18,187 MDth in 2005 but dropped to about 16,300 MDth in 2006 due to a temporary shutdown of two large cogen facilities for maintenance during the first four months of 2006. Small cogen load is expected to grow about 0.3% per year in the BCAP period, reaching 18,547 MDth by 2011.

## D.	Temperature Sensitivity (SDG&E)

Similar to SoCalGas, core demand forecasts for SDG&E are prepared for two design temperature conditions – average and cold – to quantify changes in space heating demand due to weather.  The largest demand variations due to temperature generally occur in the month of December.  Degree-day differences between the two conditions are developed from a simple average of three weather station locations to represent the San Diego service area for natural gas demand.  The cold design temperature conditions are based on a criterion that the temperature condition would be exceeded with a one-chance-in-35 annual likelihood and corresponds to 1,654 HDD for a cold design temperature year.  This contrasts to 1,306 HDD for an average design temperature year.  The average year total is the simple average of the annual (calendar year) HDD totals for the 20-year period from 1987 through 2006.  The cold year HDD value is approximately 2.025 standard deviations (standard deviation = 171.78 HDD, calculated from the same 20-year annual historical HDD data) more than the average year HDD total.

## E.	SDG&E’s Core Peak Day and Peak Month

SDG&E plans and designs its system to provide continuous service to its core customers under an extreme peak day event.  The extreme peak day design criteria are defined as a 1-in-35 annual event; this corresponds to a system average temperature of 41.8 degrees Fahrenheit (°F) or 23.2 HDD on a peak day.  Tables 16 and 17 below show the forecasted core peak day demand and the forecasted peak month demand for a cold design temperature year.

Table 16

1-in-35 Annual Likelihood (41.8°F System Avg. Temperature)

Peak Day Core Demand in MDth/day

|  | 2009 | 2010 | 2011 | 2 Year Avg. 2009-2010 | 3 Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- |
| Residential | 307 | 309 | 311 | 308 | 309 |
| C&I | 86 | 85 | 84 | 86 | 85 |
| NGV | 4 | 4 | 5 | 4 | 4 |
| Total | 397 | 398 | 399 | 397 | 398 |

Table 17

Cold Design Temperature Year: Peak Month Core Demand in MDth

|  | 2009 | 2010 | 2011 | 2 Year Avg. 2009-2010 | 3 Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- |
| Residential | 5,487 | 5,531 | 5,569 | 5,509 | 5,529 |
| C&I | 1,860 | 1,839 | 1,810 | 1,849 | 1,836 |
| NGV | 113 | 128 | 145 | 121 | 129 |
| Total | 7,460 | 7,498 | 7,524 | 7,479 | 7,494 |

# V.	COMBINED SOCALGAS & SDG&E GAS FORECASTS

## A.	Combined Peak Day Forecasts

### 1.	Combined Core Peak Day Demand Forecasts

SoCalGas and SDG&E both plan and design their systems to provide continuous service to their core customers under an extreme 1-in-35 annual event.  Table 18 shows combined core demand for such an extreme-cold 1-in-35-annual likelihood peak day.  Table 19 shows the same information, but in volumetric units of millions of cubic feet per day (MMcfd).

Table 18

Combined SoCalGas & SDG&E 1-in-35 Annual Likelihood

Peak Day Core Demand in MDth/day

|  | 2009 | 2010 | 2011 | 2 Year Avg. 2009-2010 | 3 Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- |
| SoCalGas | 3,175 | 3,179 | 3,182 | 3,177 | 3,179 |
| SDG&E | 397 | 398 | 399 | 397 | 398 |
| Combined | 3,572 | 3,577 | 3,581 | 3,574 | 3,577 |

Table 19

Combined SoCalGas & SDG&E 1-in-35 Annual Likelihood

Peak Day Core Demand in MMcfd

|  | 2009 | 2010 | 2011 | 2 Year Avg. 2009-2010 | 3 Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- |
| SoCalGas | 3,082 | 3,086 | 3,089 | 3,084 | 3,086 |
| SDG&E | 390 | 391 | 392 | 391 | 391 |
| Combined | 3,472 | 3,477 | 3,481 | 3,475 | 3,477 |

### 2.	Core Peak Day Storage: Flowing Supply and Withdrawal Capacities

Table 20 shows that the core 1-in-35 Peak Day requirement is met by a combination of firm flowing supply and core storage withdrawal rights.  SoCalGas will hold average temperature year interstate pipeline capacity of 1,090 MMcfd, to meet the Commission interstate pipeline capacity requirement per D.04-09-022, and will use it --combined with 2,225 MMcfd of core storage withdrawal, and with 162 MMcfd of other supply-- to meet SoCalGas’ and SDG&E’s core customers’ 1-in-35 Peak Day demand requirements.

Table 20

Combined SoCalGas & SDG&E 1-in-35Annual Likelihood

Peak Day Core Demand in MMcfd

| Year | 2009 | 2010 | 2011 | 2 Year Avg. 2009-2010 | 3 Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- |
| SoCalGas | 3,082 | 3,086 | 3,089 | 3,084 | 3,086 |
| SDG&E | 390 | 391 | 392 | 391 | 391 |
| Combined Demand | 3,472 | 3,477 | 3,481 | 3,475 | 3,477 |
| Avg. Year Firm Interstate Pipeline Flowing Supply | 1,085 | 1,090 | 1,094 | 1,088 | 1,090 |
| Core Storage Withdrawal | 2,225 | 2,225 | 2,225 | 2,225 | 2,225 |
| Other Supply | 162 | 162 | 162 | 162 | 162 |
| Total Supply | 3,472 | 3,477 | 3,481 | 3,475 | 3,477 |

### 3.	Combined 1-in-10 Annual Likelihood Peak Day Forecasts

Tables 21 and 22 show utility and combined core demand and total demand for a less extreme but more frequent 1-in-10 annual likelihood peak day -- under which SoCalGas is required to provide service to all customers, core and non-core.  Table 23 shows the same information as Table 22, but in volumetric MMcfd.  (In Tables 22 and 23: since SDG&E’s gas load is also part of SoCalGas’ wholesale demand, SDG&E’s end-use demand is excluded from SoCalGas’ total demand to avoid double-counting.)

Table 21

Combined SoCalGas & SDG&E 1-in-10 Annual Likelihood

Peak Day Core Demand in MDth/day

|  | 2009 | 2010 | 2011 | 2 Year Avg. 2009-2010 | 3 Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- |
| SoCalGas | 2,938 | 2,942 | 2,946 | 2,940 | 2,942 |
| SDG&E | 371 | 373 | 374 | 372 | 373 |
| Combined | 3,309 | 3,315 | 3,320 | 3,312 | 3,315 |

Table 22

Combined SoCalGas & SDG&E 1-in-10 Annual Likelihood

Peak Day Total Demand in MDth/day

|  | 2009 | 2010 | 2011 | 2 Year Avg. 2009-2010 | 3 Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- |
| SoCalGas (less SDG&E end-use) | 4,410 | 4,421 | 4,392 | 4,416 | 4,408 |
| SDG&E | 642 | 631 | 589 | 636 | 621 |
| Combined | 5,052 | 5,052 | 4,981 | 5,052 | 5,029 |

Table 23

Combined SoCalGas & SDG&E 1-in-10 Annual Likelihood

Peak Day Total Demand in MMcfd

|  | 2009 | 2010 | 2011 | 2 Year Avg. 2009-2010 | 3 Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- |
| SoCalGas (less SDG&E end-use) | 4,280 | 4,292 | 4,263 | 4,286 | 4,278 |
| SDG&E | 631 | 620 | 579 | 626 | 610 |
| Combined | 4,911 | 4,912 | 4,842 | 4,912 | 4,888 |

## B.	Combined Annual Throughput Forecasts

Table 24 shows combined annual throughput forecasts for SoCalGas and SDG&E utilities in assumed average-temperature years for the 2009-2011 BCAP period.  Table 25 shows the larger combined annual throughput under assumed cold-year conditions.

Table 24

Combined SoCalGas and SDG&E Throughput in MDth

Average Temperature Year

|  | 2009 | 2010 | 2011 | 2 Year Avg. 2009-2010 | 3 Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- |
| SoCalGas (less SDG&E end use) | 841,183 | 836,412 | 841,574 | 838,798 | 839,723 |
| SDG&E | 123,903 | 125,739 | 115,262 | 124,821 | 121,635 |
| Combined | 965,086 | 962,151 | 956,836 | 963,619 | 961,358 |

Table 25

Combined SoCalGas and SDG&E Throughput in MDth

1-in-35 Cold Year Temperature

|  | 2009 | 2010 | 2011 | 2 Year Avg. 2009-2010 | 3 Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- |
| SoCalGas (less SDG&E end use) | 871,167 | 866,466 | 871,687 | 868,817 | 869,774 |
| SDG&E | 129,169 | 131,030 | 120,568 | 130,099 | 126,922 |
| Combined | 1,000,336 | 997,496 | 992,255 | 998,916 | 996,696 |

Tables 26 and 27 show the combined utilities’ core-only annual throughput forecasts under average-temperature and cold-year-temperature conditions.

Table 26

Combined SoCalGas and SDG&E Core Throughput in MDth

Average Temperature Year

|  | 2009 | 2010 | 2011 | 2 Year Avg. 2009-2010 | 3 Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- |
| SoCalGas | 357,727 | 359,129 | 360,453 | 358,428 | 359,103 |
| SDG&E | 49,769 | 50,024 | 50,197 | 49,896 | 49,997 |
| Combined | 407,496 | 409,153 | 410,650 | 408,324 | 409,100 |

Table 27

Combined SoCalGas and SDG&E Core Throughput in MDth

1-in-35 Cold Year Temperature

|  | 2009 | 2010 | 2011 | 2 Year Avg. 2009-2010 | 3 Year Avg. 2009-2011 |
| --- | --- | --- | --- | --- | --- |
| SoCalGas | 386,342 | 387,805 | 389,178 | 387,073 | 387,775 |
| SDG&E | 55,035 | 55,315 | 55,504 | 55,175 | 55,284 |
| Combined | 441,377 | 443,120 | 444,682 | 442,248 | 443,059 |

## C.	Combined Long-Term Forecasts

Table 28 shows combined SoCalGas and SDG&E long-term forecasts through 2023. (SDG&E is included as part of Wholesale demand, since it is served through the SoCalGas system as a wholesale customer.  Also, the “Non-Core C&I” category includes EOR steaming and EOR cogeneration.) These are modified forecasts from the 2006 California Gas Report and are used in conjunction with the BCAP for long-term resource planning--discussed in the prepared direct testimony of Mr. Bisi.

Table 28

Combined SoCalGas & SDG&E Long-Term Peak Day Demand in MMcfd

|  | 1-in-35 Annual Likelihood Peak Day Demand (MMcfd) |  |  |  |  | 1-in-10 Annual Likelihood Peak Day Demand (MMcfd) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Core | N/C C&I | EG | Whole- sale | Total | Core | N/C C&I | EG | Whole- sale | Total |
| 2009/10 | 3,082 | 0 | 0 | 523 | 3,605 | 2,852 | 460 | 798 | 802 | 4,911 |
| 2010/11 | 3,086 | 0 | 0 | 528 | 3,613 | 2,856 | 460 | 803 | 793 | 4,912 |
| 2011/12 | 3,089 | 0 | 0 | 532 | 3,621 | 2,859 | 459 | 768 | 755 | 4,842 |
| 2012/13 | 3,085 | 0 | 0 | 529 | 3,615 | 2,856 | 443 | 876 | 764 | 4,940 |
| 2015/16 | 3,063 | 0 | 0 | 541 | 3,604 | 2,836 | 445 | 806 | 767 | 4,854 |
| 2020/21 | 3,030 | 0 | 0 | 558 | 3,588 | 2,805 | 438 | 1,014 | 819 | 5,076 |
| 2023/24 | 3,033 | 0 | 0 | 572 | 3,604 | 2,809 | 436 | 1,115 | 846 | 5,205 |

This concludes my testimony.

ATTACHMENT 1:  UAF STUDY

- Year 2006 Lost and Unaccounted-For

Gas at Southern California

Gas Company and San Diego Gas & Electric Company

- Year 2006 Lost and Unaccounted-For

Gas at Southern California

Gas Company and San Diego Gas & Electric Company

2006 Addendum to: “A Study of the 1991 Unaccounted-For Gas Volume at the Southern California Gas Company”

Prepared by:  Southern California Gas Company

Gas Engineering-Measurement Regulation & Control

November 30th, 2007

Table of Contents:

Topic:										        	        Page

Executive Summary							 	  		1

Table 1 - SoCalGas 2006 LUAF Gas Component Allocation 			2

Table 2 - SDG&E 2006 LUAF Gas Component Allocation 				3

Analytical Approach										4

Results and LUAF Gas Component Assignment 		  	 			5

Accounting							  	 		6

Cycle-billing, Company Use Gas, Bypass, Slow Meters			6

DR Meters, No-Close Policy							7

Other Estimated, Other Actual						8

Measurement							  	  		8

Fixed-Factor Temperature							8

Fixed Factor Pressure, Elevation and Barometric Pressure			9

Fixed Factor Calculation of Z (super compressibility)		          10

Positive Displacement Meter Accuracy				          11

Orifice Meter Accuracy						          11

Ultrasonic Meter Accuracy						          12

Turbine Meter Accuracy 						          12

Instrument Calibration Bias						          13

Ambient Temperature Effect on Instrumentation			          13

Chart Integration Bias 						          13

Leakage									          14

Distribution Leakage							          14			Transmission Leakage						          14

Theft									 	          15

Non-Study components:							          15

Conclusions:								  	  	          16

List of Appendices:

LUAF Gas Component Calculations, Methodology and Supporting Information for Line Item A-W calculation results contained in Tables 1 and 2.

Appendix:		Description

Appendix A		Cycle Billing Adjustments-no longer used

Appendix B		Company Use-Gas

Appendix C		Bypass-no longer used

Appendix D		Slow Meters

Appendix E		 DR Meters

Appendix F 		No-Close Policy

Appendix G		Other Estimated-no longer used

Appendix H		Other Actual-no longer used

Appendix I		Fixed Factor Temperature

Appendix J		Fixed Factor Pressure

Appendix K		Elevation and Barometric Pressure

Appendix L		Fixed Factor for Calculation of Z (super-compressibility)

Appendix M		Positive Displacement Meter Accuracy

Appendix N		Orifice Meter Accuracy

Appendix O		Ultrasonic Meter Accuracy

Appendix P		Turbine Meter Accuracy

Appendix Q		Instrument Calibration Bias

Appendix R		Ambient Temperature effect on Instrumentation-no longer used

Appendix S		Chart Integration Bias-no longer used

Appendix T/U		Distribution/Transmission Pipeline (and Compressor Station) Leakage

Appendix V		Theft

Appendix W		Non-Study Components (unassigned LUAF)

EXECUTIVE SUMMARY:

This document provides a summary of component and customer class allocations for Southern California Gas Company (SoCalGas) and San Diego Gas & Electric Company’s (SDG&E) lost and unaccounted-for (LUAF) gas.  The allocations are based on a review of reported year 2006 LUAF gas for the companies on areas of LUAF gas contribution as identified in a comprehensive 1991 LUAF gas study conducted by SoCalGas.   SoCalGas’ 2006 LUAF gas was 7,273,043 MMBtu, representing 0.73% of all system gas receipts  while SDG&E’s 2006 LUAF gas was 1,542,472 MMBtu, representing 1.27% of all system receipts.

Tables 1 and 2 on the following pages show year 2006 line-item core and non-core allocations of LUAF gas by component type for SoCalGas and SDG&E, respectively.  The Tables show the following allocations:

LUAF Gas Allocations: Company Core MMBtu Non-Core MMbtu Core Non-Core SoCalGas: 5,170,794 2,102,249 71.1% 28.9% SDG&E: 1,183,217 359,235 76.7% 23.3%

The analytical approach used to derive these allocations follows.

Table 1

SoCalGas 2006 LUAF Gas Component Allocation

Table 2

SDG&E 2006 LUAF Gas Component Allocation

ANALYTICAL APPROACH:

SoCalGas’ Gas Engineering Department formulated year 2006 LUAF gas components for both SoCalGas and SDG&E by employing the methods and assessment mechanics from SoCalGas’ 1991 study entitled: “A Study of the 1991 Unaccounted For Gas Volume At the Southern California Gas Company”.  This comprehensive 1991 Study, which provided the framework for SoCalGas’ LUAF gas component and customer assignment, was conducted over a two-year period.  The study incorporated detailed testing, sampling and inspection of many of SoCalGas’ metering, billing and accounting systems in 1990 and 1991.  Gas Engineering personnel reviewed the base calculations and assumptions contained in the 1991 Report and modified/updated relevant calculations with year 2006 data sets to arrive at 2006 component allocations.   The results are summarized in Table 1 for SoCalGas and Table 2 for SDG&E.   An overview of the approach used to develop these numbers is discussed in this report under the Results and LUAF Gas Component Assignment Overview section.  The specific methods, factors and calculations used to arrive at the figures in these tables are described in greater detail in Appendices A through W.  These identifying Appendix letters are mapped to the specific Line Item designations A through W in the left columns of Tables 1 and 2.

Key base-data changes from 1991 to 2006 which influenced results included the new type of meters used to serve large customers and to receive gas supplies into the system, the change in families of small meters used by SoCalGas, the location of customers and growth in the Inland areas of the service territory, and temperature differences between the analysis years.

There is no companion study of SDG&E’s LUAF gas which matches the SoCalGas 1991 study in detail and scope.  As such, SDG&E’s LUAF gas allocations for year 2006 constitute a derivative of SoCalGas’ study results, with allowances incorporated when known dissimilar utilities practices, employed technologies, or other differences, warrant acknowledgement.

The 1991 Study identified four major contributors to SoCalGas’ LUAF gas.  The four major contributors were:

- Accounting

- Measurement

- Leakage

- Theft

Within these four major contributory areas, 23 sub-components were identified.  These sub-component LUAF gas contributors have been reviewed for changes from 1991 to 2006 in operational practices, technologies, weather and other considerations.  Some sub-component derivations are still relevant today and required no alteration while others have been updated or eliminated completely.  In many instances, updated calculations to reflect differences between 1991 and 2006 data were performed to arrive at the 2006 LUAF gas components for each company.

RESULTS AND LUAF GAS COMPONENT ASSIGNMENT OVERVIEW:

Tables 1 and 2 provide a summary of specific LUAF gas components and their apportionment to the core or non-core customer classes.  Each line item (A through W) constitutes one of the 23 sub-components calculated in the 1991 report, which has been updated with 2006 data where applicable.  A summary of each sub-component and a brief description of the rationale and methodology applied to each 1991 line item to arrive at each 2006 updated LUAF gas result and customer class allocation follows:

Accounting:

A)	Cycle Billing Adjustments – This component has been removed from the LUAF gas calculation due to the fact that SoCalGas and SDG&E have controlled/adjusted for this effect by incorporating an unbilled revenue calculation several years ago.

- B)	Company - Use Gas – This is gas used by the utilities to support operations which are not metered directly or otherwise not included in operational engineering calculations.  These are very nominal volumes involving gas used for operating valves, controllers, gas measuring instruments, equipment start-up and small gas purging operations.  Appendix B shows the line item contributors to this use category.

- SoCalGas percent of LUAF: 	0.50%, 	MMBtus: 	36,176

SDG&E percent of LUAF: 	0.20%, 	MMBtus:  	  1,827

- Computed SoCalGas customer allocation is 62.9% to non-core and 37.1% to core.  SDG&E’s allocation is 59.5% to non-core and a 40.5% to core. This gas use is shared by customers based on the ratio of their aggregate class use to total system deliveries.

C)	Bypass – This is gas which bypasses meters under normal operations (e.g., testing change-outs and other related operations) where the affected gas volumes necessarily cannot be metered.    This gas is no longer unreported and unaccounted-for.  Estimates of bypass gas volume are placed on work orders. The totals from these forms are included in Company-Use Fuel ledgers.

- D)	Slow Meters – The SoCalGas year 2006 volume is based on 180,000+ small meter in-testing results and detailed testing performed on small diaphragm meters as part of the 1991 LUAF study.    This sub-component represents gas delivery which did not get billed as a result of: a) meters operating at times in slow flow ranges as a function of their design and/or as observed in empirical testing and b) meters which are removed from service, tested and confirmed as operating slow, but which do not reach the procedural threshold requiring a billing adjustment.  It includes only slow meters removed from service.  Known meter families which run slow but which remain in service are covered under Line item “M” – Positive Displacement Meter Accuracy.  This statistically negligible Slow Meter component has shown virtually insignificant change since the 1991 Study.  Slow meter-associated LUAF gas was calculated for SDG&E by applying SoCalGas’ meter testing results to SDG&E’s similar family in-service meter populations.

- SoCalGas percent of LUAF: 	<0.00%, 	MMBtus: 	312

SDG&E percent of LUAF:	<0.00%, 	MMBtus: 	  38

Allocation for this slow meter volume is 100% to the core market for both utilities.  Slow meter considerations affecting larger meter technologies serving non-core customers are covered under other specific metering categories in this report.

- E)	Did Not Register (DR) Meters – The SoCalGas 2006 volume is based on actual 2006 customer billing adjustments associated with small meters which failed and required replacement.  This sub-component has shown insignificant change at SoCalGas since 1991.  DR meter LUAF gas was calculated for SDG&E based on SoCalGas’ proportion of LUAF gas for the same meter categories.

- SoCalGas percent of LUAF: 	0.05%, 	MMBtus: 	3,353

SDG&E percent of LUAF: 	0.03%, 	MMBtus:      	   410

- Assignment is 100% to core customers for this component, as any required DR meter adjustments affecting non-core customers are performed directly for each non-core meter site.

- F)	Authorized No-Close Policy – The 2006 SoCalGas allocation is based on 2006 recorded data from SoCalGas' billing system and has shown significant change since the 1991 study due to residential customer growth and expansion of the no-close process.  The policy was merely a pilot study in 1991.  This 2006 component was calculated by taking the aggregate of initial meter reads when a new customer moves into a location and subtracting the final meter reads associated with the previous customer’s usage.  The results of these calculations are shown below.

- SoCalGas percent of LUAF:  6.77%, 		MMBtus:	 492,115

SDG&E percent of LUAF:   	3.92%,		MMBtus:           60,400

No close policy LUAF gas is assigned fully to core customers, as they are the customer group for which this practice is authorized.

- G)	Other Estimated – This is no longer a calculated LUAF gas sub-component.  The 2006 allocation is zero for both companies.

- H)	Other Actual – This is no longer a LUAF gas sub-component due to changes in measuring, estimating and accounting practices. The 2006 allocation is zero for both companies.

Measurement:

I)	Fixed-Factor Temperature – This component represents the over-registration of small gas meters without gas temperature correction.  In 2006, the net effect was to lower overall LUAF gas.  Customer growth in the Inland area and warmer temperatures in year 2006 were the major causes which changed this number by 10% from 1991 levels for SoCalGas.  SDG&E’s component was apportioned based on relative numbers of meters which are subject to this phenomenon in comparable temperature zones.

- SoCalGas percent of LUAF:	 -21.83%,	MMBtus:	 -1,587,947

SDG&E percent of LUAF:	 -11.62%, 	MMBtus:   	    -179,281

This entire component is assigned to core customers.  Non-Core customers’ meters ordinarily have compensation for both flowing gas pressure and temperature.

J)	Fixed-Factor Pressure – This component represents under-billing which occurs due to gas regulation pressure upstream of meters being higher than the as-billed pressure.  Based on the results of regulator inspections in 2006, the average fixed factor pressure customer still experiences this slight under-registration.

- SoCalGas percent of LUAF:	 4.43%,     	MMBtus:	 322,501

SDG&E percent of LUAF: 	 3.30%, 	MMBtus:	   50,905

This component is assigned 100% to core customers as non-core customers have electronic devices which measure and compensate for meter pressure (see Line Item “Q” - Instrument Calibration Bias discussion below.)

K)	Elevation and Barometric Pressure – Elevation-based LUAF gas results from the elevation where customers actually are served, in the aggregate, being slightly different than the mean altitude assumed in their billing “altitude zone”- used for billing standard pressure customers or "elevation zone"- used for above standard pressure customers.  When the aggregate of customers within a zone are situated at an altitude below the mean elevation of that zone used for barometric pressure billing correction, customers on average are under-billed.  When they reside above the elevation zone median, their delivered gas pressure is slightly less than assumed, and thus a slight over-registration occurs.

An analysis of each of SoCalGas elevation and altitude zone was performed in 1991.  The results showed that customers were on-average situated slightly below their zone mean resulting in higher delivery pressure (and barometric pressure) than employed in billing calculations.   SoCalGas 2006 data for this component was calculated by applying updated meter and load information for each of eight standard pressure Altitude Zones (1000' increments) where statistical determination of customer elevation was performed in 1991.  This result was applied to standard pressure customer volumes to compute a 2006 result. A similar analysis was performed for above standard pressure customers by updating information for each of 16 "elevation zones" (400' increments).  The contributions to LUAF gas for this phenomenon in 2006 were as follows:

- SoCalGas percent of LUAF: 	17.10%, 	MMBtus: 	1,243,910

SDG&E percent of LUAF: 	12.83%, 	MMBtus:    	   197,879

SDG&E LUAF contribution was computed by applying SoCalGas altitude zone elevation biases for comparable SDG&E geographic areas.    This gas LUAF component is assigned 100% to the core market, as non-core accounts are assigned a barometric read which is site specific, or the pressure at the metering site is an absolute reading from an electronic transmitter registering in units of absolute pressure.

L)	Fixed-Factor For Calculation of Z – Bias associated with the fixed factor calculation of super-compressibility changed from 1991, as the temperature associated with the delivery of gas to this class of customers was slightly different.   This calculated bias occurs because the assumed system temperature used for the small customer super-compressibility calculation is 60 degrees Fahrenheit while the actual average gas temperature is approximately 64 degrees Fahrenheit for affected meter sets.  This resulted in some minor over-registration of gas flows.    SDG&E’s LUAF gas was calculated using the same method, using a gas temperature of 62.7 degrees F and applying the results to fixed temperature SDG&E customer volumes. The resulting LUAF gas reductions are as follows:

- SoCalGas percent of LUAF:	 -0.64%, 	MMBtus: 	-46,371

- SDG&E percent of LUAF:	 -1.07%, 	MMBtus:   	-16,445

- This component is allocated 100% to core customers, as non-core customer’s super-compressibility and volumes are computed using the measured flowing gas temperature at the meter site.

- M)	Positive Displacement Meter Accuracy – This LUAF gas component reflects the impact of small meter families which have been shown to run slow,  but which remain in service as they are not outside of SoCalGas and SDG&E’s, CPUC-approved,  Meter Performance Control Program criteria for replacement.   The LUAF contributions are based on the in-testing of 180,000 meters and applying the results to both SoCalGas and SDG&E in-service meter families in order to statistically compute the system-wide impact of slow meters.  Testing of meter performance at different flow rates and matching of registration biases with customer use profiles was also used to determine this LUAF contribution.  Since the 1991 study, many slow meter families have been taken out of service resulting in a reduction in LUAF gas for this sub-component.

- SoCalGas percent of LUAF: 	31.84%, 	MMBtus: 	2,315,574

SDG&E percent of LUAF: 	35.90%, 	MMBtus: 	   553,681

This component is assigned 100% to core customers, since those customers are affected exclusively by the Meter Performance Control Program.

N)	Orifice Meter Accuracy – There has been a migration of some SoCalGas retail and receipt-point orifice meters to ultrasonic meters since 1991.  This includes the meters at the primary interconnection between SoCalGas and SDG&E at Rainbow.    The net effect is a reduction in SoCalGas LUAF gas as a result of fewer “slow” orifice meters at retail delivery locations.  SDG&E has a lesser percentage of retail deliveries through orifice meters compared to SoCalGas.  SDG&E’s largest orifice meter impact is from its gas receipt point at San Onofre.  Slight under-measurement of this meter results in a favorable LUAF gas component for SDG&E.

- SoCalGas percent of LUAF: 	58.69%, 		MMBtus: 4,268,399

SDG&E percent of LUAF: 	-1.72%, 		MMBtus:    -26,505

This component is assigned to both core and non-core customers based on volume weighted orifice-meter supplies and retail delivery meters considerations.  All customer class’ supplies are received by orifice meters, but only non-core customers are served by this metering technology.

O)	Ultrasonic Meter Accuracy – SoCalGas’ finding is that ultrasonic meters can exhibit a positive calibration shift over time and also can exhibit a bias from calibration factor parameters when operating with a single meter factor (and operating at lower than average flow rates.)  Maintenance work and repair can also have an upward bias of such metering when probes are replaced in the field due to failure.  SoCalGas has used its field findings to project minor upward bias on some of its ultrasonic meters.    The associated 2006 LUAF gas impact are:

- SoCalGas percent of LUAF:	 -2.92%,	MMBtus: 	 -212,298

SDG&E percent of LUAF:	 33.58%, 	MMBtus:   	  517,910

The allocation of this component to customers is a volume-weighted calculation which takes into consideration that both core and non-core customers receive their gas into SoCalGas and SDG&E’s transmission lines via ultrasonic meters, while all direct retail deliveries to customers via such meters are for non-core service only.   The SoCalGas LUAF gas allocation is a 441,261 MMbtu credit to the non-core market and a 228,963 MMBtu LUAF gas contribution to the core market.  The SDG&E LUAF gas allocations are 232,171 MMbtu to the non-core market and a 285,739 MMBtu to core customers.

- P)	Turbine Meter Accuracy – This component is based on the results of lab calibration tests for meters removed from service and includes field calibration (Aux) factor consideration, which places the lab calibration bias number in the field devices to provide true zero meter error upon installation.  Overall these results show a slight over-registration effect for turbine meters in 2006.     SDG&E’s turbine meter-associated LUAF gas was based on similar results and also compensated for the fact that SDG&E does not include a meter aux factor in its field configuration.

- SoCalGas percent of LUAF: 	-11.32%, 	MMBtus: -823,111

SDG&E percent of LUAF: 	 -4.83%,	 MMBtus:  -74,450

This component is assigned 97% to non- core customers for both utilities, based on the volume weighting of customers served by turbine meters.

- Q)	Instrument Calibration Bias – This component is calculated from actual field audits performed in 2006 (using “as-found” data from electronic instruments providing pressure and temperature correction for large customers) and now includes the sub-component Ambient Temperature Effect on Instrumentation.

- SoCalGas percent of LUAF: -3.72%, 	MMBtus: 	-261,961

SDG&E percent of LUAF:   -0.75%, 		MMBtus: 	  -11,522

This component is assigned 99% to SoCalGas' non-core customers, based on the error type associated with the specific equipment in-service at the different customer classes and volume weighting the allocated bias effect.  The allocation to SDG&E's non-core customers is 89% based on symmetric criteria.

- R)	Ambient Temperature Effect on Instrumentation – Ambient temperature effect is now included in the above referenced subcomponent “Instrument Calibration Bias”.

- S)	Chart Integration Bias – Charts are an outdated technology and are no longer used for custody transfer billing.  The 2006 LUAF gas component contribution is zero for both utilities.

- Leakage:

T)	Distribution Leakage – Year 2006 leakage data for mains and services was derived from 2006 mileage, pipe type and updated leak per mile factors for the associated pipe.  SDG&E’s pipeline leakage rate were computed in the same manner as SoCalGas', with SDG&E’s miles of pipe used instead of SoCalGas.  Details are provided in Appendix T/U.

- SoCalGas percent of LUAF: 8.04%, 		MMBtus: 584,817

SDG&E percent of LUAF:   6.55%, 		MMBtus: 101,106

The allocation to customer class for both companies was computed based on the relative volume of gas used by core and non-core customers served off of the distribution system.  The allocation for distribution leakage is 76% core and 24% non-core for both utilities.

- U)	Transmission Leakage – SoCalGas 2006 LUAF gas attributable to this component was derived by adjusting transmission pipeline mileages between 1991 and 2006 and applying the 1991 per mile leak rate.  Leakage for compressor stations was computed by using 1991 Mcf/hour leak factors for each compressor station with actual 2006 operational hours used as the multiplier.  SDG&E’s 2006 LUAF gas for this component was computed using SDG&E’s pipeline mileage and comparable-type SoCalGas leak factors for pipeline contribution.  Comparable SoCalGas compressor leakage rates and SDG&E’s actual operating hours were used to compute SDG&E’s compressor station contributions.

- SoCalGas percent of LUAF: 	0.42%, 		MMBtus: 	30,698

SDG&E percent of LUAF: 	0.19%, 		MMBtus: 	  2,999

Transmission pipelines and compressors serve all customers; as such gas LUAF gas component allocations are based on customer class percentage of total gas deliveries.   The results are:  SDG&E: non-core 59% and core 41%; SoCalGas: non-core 63% and core 37%.

Theft:

V)	Theft – Two calculation methods were used in the 1991 study and the method with the larger amount of LUAF gas was chosen for the analysis in that era.  After updating these calculations for customer growth and other factors in 2006, an average of the two calculation methods (entailing percentage of customers who steal gas and the average amount per episode) was used for this revision, resulting in a slight decrease in the percentage of this sub-component.  Theft component LUAF contribution was calculated for SDG&E by applying SoCalGas’ customer behavior findings/results to SDG&E customer meter counts.

SoCalGas percent of LUAF: 	5.64%, 	MMBtus: 	409,872

SDG&E percent of LUAF: 	3.57%, 	MMBtus: 	  55,075

Theft-related LUAF gas allocation was allocated to core and non-core customers based on residential/non-residential end use designation use in the theft calculations.  Residential theft was assigned to core while non-residential theft was assigned to non-core for both Companies.  The results are:  SoCalGas: non-core 32%, core 68%; and SDG&E: non-core 26%, core 74%.

Non-Study Components:

W)	Non-Study Components – This category represents the remainder of LUAF gas for each utility which has not been specifically assigned to a known LUAF gas contribution area.  It represents those contributions which might be assignable in any of the other areas, but for which more study would be required to provide such definitive allocations.  These numbers also represent the practical limits of certainty for each of the utilities’ LUAF gas analyses.

SoCalGas percent of LUAF: 6.95%, 		MMBtus: 	505,303

SDG&E percent of LUAF: 19.92%,  		MMBtus: 	307,197

Non-study components were assigned to customer class based on aggregate customer class energy use in 2006.

CONCLUSIONS:

SoCalGas’ 2006 LUAF gas was 7,273,043 MMBtu, representing 0.73% of all system deliveries; while SDG&E’s 2006 LUAF gas was 1,542,472 MMBtu, constituting 1.27% of all system deliveries.   Assignment of these LUAF gas figures to customer class, based on the volume-weighted results of all sub-component allocations, is as follows:

Description						SoCalGas      		 	SDG&E:

2006 LUAF MMBtu					7,273,043			1,542,472

Core Allocation MMBtu				5,170,794		 	1,183,237

Non-Core Allocation MMbtu			 2,102,249		  	   359,235

Core Allocation%       	     	               	     71.1%			     76.7%

Non-Core Allocation%	    	                    	     28.9%			     23.3%

APPENDIX A

Cycle Billing Adjustments

Cycle billing adjustment was historically used to refine the formal annual LUAF number for end of year and beginning of year meter reads.  This component has been removed from the LUAF gas calculation due to the fact that SoCalGas and SDG&E  controlled/adjusted for this effect by incorporating an unbilled revenue calculation into the reported LUAF numbers several years ago.  It is integral to the reported number.

APPENDIX B

Company Use Gas

Company use gas LUAF contribution is associated with gas which is used in operations but not sufficiently large enough to report on special accounting forms.  Volume II (Accounting-P.43) of the 1991 LUAF study discusses the SoCalGas Company Use gas LUAF contribution of 61,928 Mcf in that year and the method employed to arrive at this figure.  The base methodology for calculating Company Use gas LUAF in 2006 remained unchanged for 2006, although several technology changes from 1991 to 2006 did impact this figure favorably.  High-bleed gas quality measurement devices have been replaced by gas chromatographs.  Turbine start figures have been reduced substantially as gas used for such purposes is now measured for most of the two companies' gas turbine-driven compressors.  Tables B-1 and B-2 show the data sets and calculation results for this gas LUAF component in 2006 for SoCalGas (35,065 Mcf : 36,176 MMBtu) and SDGE (3,021 Mcf : 3,074 MMBtu), respectively.

Table B-1

Table B-2

Allocation to customer class for each company is based on 2006 relative delivered energy to core and non-core customers.

APPENDIX C

Bypass Gas LUAF

Bypass gas contribution to gas LUAF, as reported in 1991, is now fully reported and accounted for in Company Use gas for 2006.  As a result, it is no longer a LUAF component for SoCalGas.  It is similarly not a LUAF component for SDG&E in 2006.

APPENDIX D

Slow Meter Gas LUAF

Slow Meter gas LUAF contribution is associated with gas meters which have been in-tested (after removal from a customers premise, approximately 180,000 per year) and found to be operating slow, but which are below the threshold for SoCalGas/SDGE to provide the customers billing adjustments.

Volume II (Accounting-P.69) of the 1991 LUAF study discusses the Slow Meter gas LUAF contribution of 246 Mcf in that year.  Accounting processes for calculating Bypass gas LUAF in 2006 remained unchanged.  The value is simply the summation of all identified slow meters which were not re-billed as-compiled in CIS report E12P02-3 LUAF.  The 2006 value, shown below in Table D-1 is 302.3 Mcf.  SDG&E slow meter data was calculated using SoCalGas LUAF and multiplying by the ratio of contributing meter types/sizes between the two companies.  The SDGE contribution is 38 Mcf.

Table D-1

| Slow Meter Allowance |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | 302.3 MCF/Year for 2006 |  |  |  |  |
| Source |  |  |  |  |  |
|  | System Report: E12P02-3 Allowances Report |  |  |  |  |
| Definition |  |  |  |  |  |
|  | Slow meter volumes not billed |  |  |  |  |
| Explanation |  |  |  |  |  |
|  | This report identified slow meter volumes marked as |  |  |  |  |
|  | too small to rebill. |  |  |  |  |
|  | A residential meter that is less than 25% slow |  |  |  |  |
|  | or when the calculated unregistered volume |  |  |  |  |
|  | is 25 ccf or less is not rebilled |  |  |  |  |
|  | A non-residential meter that is less than 2% slow |  |  |  |  |
|  | or when the calculated unregistered volume |  |  |  |  |
|  | is 25 ccf or less is not rebilled |  |  |  |  |

As-found slow meters which do not trigger billing adjustments are generally limited to small volume use meters and customers.  Therefore this component is assigned 100% to core customers for both Companies.

APPENDIX E

DR Meter Gas LUAF

DR Meter gas LUAF contribution is associated with gas meters serving customers which do not register and are removed, but for which estimated volumes are not fully billed to customers due to billing procedural requirements - estimated quantity less than 25 ccf.

The 1991 LUAF study discusses the DR gas LUAF contribution of 5,008 Mcf in that year.  Accounting processes for calculating DR Meter gas LUAF gas LUAF in 2006 remained unchanged at SoCalGas. The DR Meter 2006 gas LUAF component is the summation of all DR gas estimates as-compiled in CIS report E12P02-3 LUAF.  Table E-1 below, and excerpt from this report, shows this value to be 3,250 Mcf (3,353 MMBtu).

E-1

SDG&E DR meter data was calculated using SoCalGas LUAF and multiplying by the ratio of contributing meter types/sizes between the two companies.  The 2006 SDGE gas LUAF contribution associated with DR meters was 403 Mcf (410 MMBtu).

DR Meter gas LUAF is allocated 100% to core customers, as non-core customers DR meters are identified and fully reconciled for billing purposes.

APPENDIX F

No-Close Policy gas LUAF

No Close gas LUAF contribution is associated with authorized procedures which allow both companies to leave gas service active when customers vacate a premise.  The gas use (typically pilot lights) at a facility between the time a customer moves out and the subsequent occupant orders gas service is not billed to any customer.  The result is a significant LUAF contribution attributable to this phenomenon.  The total contribution for this Policy is calculated in SoCalGas’ CIS report E12P02-5 LUAF to be 477,006 MCF (492,115 MMBtu).  This policy was a partial year pilot program in 1991 and the LUAF contribution much lower in that year (3,479 Mcf).

Table F-1

Summary of CIS billing system No Close Meter Registration differentials.

| LUAF Due to No Close Policy |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 477,005.7 MCF/Year for 2006 |  |  |  |  |  |
| Source |  |  |  |  |  |  |
|  | System Report: E12P02-5 LUAF Report |  |  |  |  |  |
| Definition |  |  |  |  |  |  |
|  | Usage recorded by the meter at a vacant facility. |  |  |  |  |  |
| Explanation of Report Categories |  |  |  |  |  |  |
|  | Usage between the off date and hard meter close date |  |  |  |  |  |
|  | is recorded as "Soft Close" LUAF |  |  |  |  |  |
|  | Usage resulting from a leak at the meter on a vacant |  |  |  |  |  |
|  | facility is recorded as "Leakage on an Off Meter". |  |  |  |  |  |
|  | Usage between the off date for one customer and |  |  |  |  |  |
|  | On date for another customer is recorded as "LUAF" |  |  |  |  |  |
|  | Usage between hard meter close date and new |  |  |  |  |  |
|  | customer on date is recorded as "Unauthorized Usage |  |  |  |  |  |
|  | no customer to bill" |  |  |  |  |  |

SDG&E No Close Policy LUAF contribution data was calculated using SoCalGas LUAF volumes and multiplying by the ratio of contributing meter types/sizes between the two companies.  The Soft close policy impacts are symmetric for the two companies.  The SDGE contribution is 59,368 Mcf.  Soft Close is allocated 100% to core customers as they are the class of customer for which this policy is authorized.

APPENDIX G

Other Estimated

This Component is no longer considered LUAF in 2006.  Corrections made to customer bills are fully reconciled as company credit/debit on gas ledgers, regardless of time skew.

APPENDIX H

Other Actual Gas Usage

This Component is no longer characterized as gas LUAF; it is accounted for or otherwise estimated and represented as Company Use on gas ledgers.

APPENDIX I

Fixed-Factor Temperature Gas LUAF

Fixed Factor Temperature gas LUAF results when actual gas temperature at a customer meter is something other than 60 degrees F, the value upon which customers without temperature compensating meters are billed.    In 2006 the average gas temperature at small customer meters was calculated on the SoCalGas to be 62.08 degrees, resulting in slight over-billing of small meter customers in the aggregate.  The average at larger meters was 63.72.  For SDG&E the temperatures for small meters averaged 61.5 degrees F, while larger fixed factor temperature meters averaged 62.79.   Larger fixed factor meters, serving processes and production activity as opposed to domestic use, have less variation in delivered volumes between summer and winter than smaller meters.   Their relative use does not drop off as much in summer, resulting in higher volume-weighted average gas temperatures.

- Discussion:

- The 2006 Fixed Factor Temperature LUAF contribution for SoCalGas employed the method presented in the following 1991 LUAF Measurement report Tables.

Fixed-Factor Temperature UAF at Small Meters		Table 3.1.1-2

Fixed-Factor Temperature UAF at Large Meters		Table 3.1.1-3

This method was updated with 2006 customer volume and zone gas temperature data.

In the elements of Fixed-Factor Temperature at Small and Large Meters and Fixed-factor Pressure at Standard Delivery Pressure, it was determined that the methodology of 1991 was correct, but the conditions in 2006 had changed and warranted a verification that the Temperature and pressure findings were still applicable.

In regards to Fixed-factor temperature at Small and Large meters, there are now 3 Billing Zones instead of 6 Weather Zones as in 1991.  The 2006 monthly volume for small and large meters for each Billing Zone and the average monthly ambient temperature for each Billing Zone were required to calculate the 2006 UAF for this element. The increase in 2006 vs. 1991 UAF (gain due to over-registration) for Fixed Factor temperature was due to an increase in the average gas temperature.  The gas temperature increased from 60.6 in 1991 to 62.8 degrees F for small meters in 2006.  Table I-1 below shows the 2006 volume weighted temperature calculation for each billing zone.

Table I-1:

Fixed Factor Temperature Zone data  (small meters core size 1-3)

| Months 2006 Size 1-3 Meters | Zone 1 Monthly Temp Basin | Zone 2 Monthly Temp Foothill/Central | Zone 3 Monthly Temp Mountain | Zone 1 Monthly Volume (MCF) | Zone 2 Monthly Volume (MCF) | Zone 3 Monthly Volume (MCF) |
| --- | --- | --- | --- | --- | --- | --- |
| January | 57.13 | 50.85 | 37.88 | 28,607,140 | 3,113,444 | 235,179 |
| February | 58.98 | 53.05 | 39.44 | 24,775,664 | 2,638,099 | 209,398 |
| March | 54.48 | 51.07 | 35.13 | 28,292,914 | 2,805,513 | 238,889 |
| April | 60.21 | 58.28 | 44.51 | 19,738,166 | 1,819,751 | 201,971 |
| May | 67.25 | 68.47 | 53.35 | 14,194,073 | 1,103,071 | 84,143 |
| June | 74.51 | 75.84 | 63.79 | 11,894,148 | 880,932 | 50,682 |
| July | 80.47 | 81.7 | 69.45 | 10,135,585 | 799,517 | 40,851 |
| August | 75.47 | 75.83 | 65.23 | 10,017,561 | 790,645 | 38,691 |
| September | 73.79 | 72.21 | 60.22 | 10,906,293 | 888,200 | 49,165 |
| October | 67.07 | 62.88 | 50.04 | 12,337,124 | 1,078,415 | 87,069 |
| November | 64.39 | 57.35 | 46.42 | 16,632,589 | 1,778,166 | 131,505 |
| December | 56.85 | 49.18 | 37.35 | 28,133,204 | 3,250,625 | 233,971 |
| Total Mcf each Zone |  |  |  | 215,664,461 | 20,946,378 | 1,601,514 |
| Volume weighted average zone temp (degrees F) | 62.78 | 57.71 | 43.58 |  |  |  |
| Total Volumes (Mcf) of all Zones: |  |  |  |  |  | 238,212,353 |
| # of Meters per Zone |  |  |  | 4,932,677 | 450,557 | 25,411 |
| weighted gas temperature | 62.08 |  |  |  |  |  |

Table I-2 shows the resulting 2006 reduction to LUAF based on this zone deviation in gas temperature from 60 degrees F.  This value is -951,824 Mcf (LUAF reduction).

Table I-2

Size 1-3 Meters

| Months 2006 | Zone 1 Monthly UAF % | Zone 2 Monthly UAF % | Zone 3 Monthly UAF % | Zone 1 Monthly UAF Volume (MCF) | Zone 2 Monthly UAF Volume (MCF) | Zone 3 Monthly UAF Volume (MCF) |
| --- | --- | --- | --- | --- | --- | --- |
| January | 0.555% | 1.792% | 4.446% | 158867 | 55802 | 10456 |
| February | 0.197% | 1.356% | 4.119% | 48725 | 35760 | 8626 |
| March | 1.074% | 1.748% | 5.026% | 303757 | 49053 | 12007 |
| April | -0.040% | 0.332% | 3.072% | -7973 | 6043 | 6205 |
| May | -1.376% | -1.604% | 1.296% | -195299 | -17690 | 1091 |
| June | -2.716% | -2.958% | -0.724% | -323082 | -26057 | -367 |
| July | -3.790% | -4.008% | -1.786% | -384114 | -32047 | -730 |
| August | -2.891% | -2.956% | -0.996% | -289591 | -23372 | -386 |
| September | -2.585% | -2.296% | -0.042% | -281929 | -20390 | -21 |
| October | -1.342% | -0.551% | 1.954% | -165591 | -5944 | 1701 |
| November | -0.838% | 0.513% | 2.683% | -139330 | 9114 | 3529 |
| December | 0.610% | 2.126% | 4.557% | 171570 | 69120 | 10662 |
| Summary | -0.512% | 0.475% | 3.295% | -1,103,989 | 99,391 | 52,774 |
| Weighted LUAF contribution for all zones-small meters |  |  | 0.40 | TOTAL Small Meter LUAF Zones 1-3 (Mcf |  | -951,824 |

Table I-3 shows temperature data for large core meter (size 4 meters and larger).  These meters have a different geographic distribution and customer use profile which results in a 2006 average gas temperature of 63.72 degrees F.

Table I-3:

Fixed Factor Temperature gas LUAF (Large meters size core 4+)

2006 UAF Summary Fixed-Factor Temperature UAF at Large Meters

| Months 2006 Size 4&up Meters | Zone 1 Monthly Temp Basin | Zone 2 Monthly Temp Foothill/Central | Zone 3 Monthly Temp Mountain | Zone 1 Monthly Volume (MCF) | Zone 2 Monthly Volume (MCF) | Zone 3 Monthly Volume (MCF) |
| --- | --- | --- | --- | --- | --- | --- |
| January | 57.13 | 50.85 | 37.88 | 8,217,370 | 760,380 | 18,108 |
| February | 58.98 | 53.05 | 39.44 | 7,522,001 | 685,267 | 17,453 |
| March | 54.48 | 51.07 | 35.13 | 8,103,237 | 698,356 | 19,082 |
| April | 60.21 | 58.28 | 44.51 | 6,788,903 | 518,655 | 15,975 |
| May | 67.25 | 68.47 | 53.35 | 5,828,766 | 408,145 | 9,444 |
| June | 74.51 | 75.84 | 63.79 | 5,147,656 | 400,502 | 7,106 |
| July | 80.47 | 81.7 | 69.45 | 4,636,873 | 402,008 | 6,415 |
| August | 75.47 | 75.83 | 65.23 | 4,626,831 | 399,785 | 6,484 |
| September | 73.79 | 72.21 | 60.22 | 4,961,077 | 416,496 | 7,476 |
| October | 67.07 | 62.88 | 50.04 | 5,437,476 | 445,523 | 9,201 |
| November | 64.39 | 57.35 | 46.42 | 6,338,021 | 552,429 | 11,847 |
| December | 56.85 | 49.18 | 37.35 | 8,066,697 | 800,781 | 18,701 |
| Large Meter Zone totals (Mcf) |  |  |  | 75,674,908 | 6,488,327 | 147,292 |
| Volume weighted average Zone temp (degrees F) | 62.78 | 57.71 | 43.58 |  |  |  |

The associated gas LUAF gain for large meters, as shown in calculation summary Table I-4, is -587,368 Mcf.

Table I-4

| Months 2006 Size 4&up Meters | Zone 1 Monthly UAF % | Zone 2 Monthly UAF % | Zone 3 Monthly UAF % | Zone 1 Monthly UAF Volume (MCF) | Zone 2 Monthly UAF Volume (MCF) | Zone 3 Monthly UAF Volume (MCF) |
| --- | --- | --- | --- | --- | --- | --- |
| January | 0.555% | 1.792% | 4.446% | 45634 | 13628 | 805 |
| February | 0.197% | 1.356% | 4.119% | 14793 | 9289 | 719 |
| March | 1.074% | 1.748% | 5.026% | 86998 | 12210 | 959 |
| April | -0.040% | 0.332% | 3.072% | -2742 | 1722 | 491 |
| May | -1.376% | -1.604% | 1.296% | -80199 | -6546 | 122 |
| June | -2.716% | -2.958% | -0.724% | -139826 | -11847 | -51 |
| July | -3.790% | -4.008% | -1.786% | -175726 | -16114 | -115 |
| August | -2.891% | -2.956% | -0.996% | -133754 | -11818 | -65 |
| September | -2.585% | -2.296% | -0.042% | -128244 | -9561 | -3 |
| October | -1.342% | -0.551% | 1.954% | -72983 | -2455 | 180 |
| November | -0.838% | 0.513% | 2.683% | -53093 | 2831 | 318 |
| December | 0.610% | 2.126% | 4.557% | 49195 | 17028 | 852 |
|  | -0.780% | -0.025% | 2.860% | -589,948 | -1,632 | 4,212 |
| Summary | UAF% Zone 1 | UAF% Zone 2 | UAF% Zone 3 | Zone 1 UAF | Zone 2 UAF | Zone 3 UAF |
| 2006 UAF Fixed T Large |  | -587,368 | 1991 UAF Fixed T Large |  |  | -1,470,933 |
| 2006 Vol by Zone MCF |  | 82,310,527 | 1991 Vol by Zone MCF |  |  | 83,268,184 |
| 2006 UAF % by Zone 2006 Avg. T Large |  | -0.71% 63.72 F | 1991 UAF % by Zone 1991 Avg. T Large |  |  | -1.77% 69.2 F |

Total 2006 SoCalGas Fixed Factor Temperature gas LUAF reduction for both small and large core meters combined was 1,539,192 Mcf.

SDG&E:

SDG&E gas LUAF contribution associated with Fixed Factor Temperature phenomena was calculated by applying SoCalGas Temperature zone data to SDG&E deliveries by- month to SDGE zone volumes.  The computed average temperature for SDGE small meters was 61.5 degrees F, while the computed average for large meters was 62.79 degrees F.  Table I-5 shows the results of the volume and zone temperature weighted calculations.

Table I-5

SDG&E 2006 LUAF Fixed Factor Temperature
Analysis – Average Gas Temperature Results.

| Year 2006 SDG&E Avg T (degrees F) | 64.54 |
| --- | --- |
| Est. SDGE 2006 T vol wt Small Meters (deg F) | 61.5 |
| Est. SDGE % UAF Small Meter (1.5/520) | -0.29% |
| Est. SDGE 2006 T vol wt Large | 62.79 |
| Est. SDGE % UAF Large Meter (2.79/520) | -0.53% |

Table I-6 below shows the calculated gas LUAF associated with fixed factor temperature billing phenomena for both small and larger meters.    The associated volume weighted gas LUAF reduction is shown to be -83,731 for small meters and -92,486 for large core meters for a total LUAF reduction of 176,217 Mcf.

Table I-6

| Fixed T Small Meters | 2006 Volume MCF | Fixed T Small UAF% SDGE 2006 | SDG&E 2006 UAF Volume Mcf |
| --- | --- | --- | --- |
| Small Diaphragm | 28,709,290 | -0.29% | -83,257 |
| Small Diaphragm TG | 163,518 | -0.29% | -474 |
| (Use SCG Small Meter UAF% Zone 2) |  |  |  |
| Total Fixed T Small | 28,872,808 | -0.29% | -83,731 |
| Fixed T Large Meters |  |  |  |
| Large Diaphragm | 3,441,982 | -0.53% | -18,243 |
| Rotary w/o TC | 6,769,135 | -0.53% | -35,876 |
| Large Diaphragm TG | 378,924 | -0.53% | -2,008 |
| Rotary TG w/o TC | 5,789,354 | -0.53% | -30,684 |
| Turbine TG - no TC | 1,070,770 | -0.53% | -5,675 |
| (Use SCG Large Meter UAF% Zone 2) |  |  |  |
| Total Fixed T Large | 17,450,165 | -0.53% | -92,486 |
| SDG&E UAF Fixed T 2006 | 46,322,973 | -0.38% | -176,217 |

The allocation of Fixed Factor Temperature gas LUAF reduction is 100% to core customers for both SoCalGas and SDG&E, as non-core customers are equipped with temperature compensating metering devices.

APPENDIX J

Fixed Factor Pressure gas LUAF

The method for calculating LUAF contribution for this component was to apply measured 2006 regulator field pressure tests results and observed biases to fix-factor metered volumes for both SDGE and SoCalGas.  These volumes were obtained from the CIS and CISCO billing systems.  When the actual pressure delivered to a gas meter is higher than that assumed in fixed factor billing calculations, the associated gas meter under-registers by a small amount.  In 2006, the net effect was to under-register by approximately 0.1%.  This was due to average regulator standard pressure accounts being served at 8.51 inches water column while billing pressure was 8.0 inches.  The results constitute an update of Table 3.1.2-1 in Volume III (Accounting-P.26) of the 1991 LUAF study.  Fixed Factor Pressure gas LUAF contribution in that year was 271,007.

Year 2006 findings for small meter sets were based on 631 sampled regulators from a special field study and normal QC receiving inspection test results.  Observed meter pressured biases were applied to associated customer volumes.

Table J-1 below shows the net Fixed Pressure gas LUAF contribution for SoCalGas to be 312,599 Mcf in 2006.

Table J-1

2006 UAF Summary SoCalGas Fixed-Factor Pressure for
Standard Pressure and Temporary Gauge Meter Sets

| Category | Avg Delivery Pressure (in. w.c.) | 2006 Del Vol Sample TG Sets | 2006 UAF Vol Sample Sets | Delivery Pressure Correction Factor | 2006 System Delivery Volume (MCF) | 2006 UAF Volume (MCF) |
| --- | --- | --- | --- | --- | --- | --- |
| Small Meters 8" w.c. | *8.51 | n/a | n/a | 1.0012 | 237,276,951 | 290,892 |
| Large Meters 8" w.c. | **8.40 | n/a | n/a | 1.0010 | 48,073,468 | 46,224 |
| Temporary Gauge Sets | n/a | 7,583,868 | -13,600 | 0.9982 | 13,671,928 | -24,518 |
| 2006 Totals |  |  |  | 0.10% | 299,022,347 | 312,599 |

SDG&E:

SDE&E Fixed Factor Pressure gas LUAF volumes were computed using SoCalGas and SDG&E regulator sampling results and applying them to SDG&E volumes subject to this phenomenon.  The result is shown below in Table J-2 to be 50,035 Mcf.

Table J-2

2006 UAF Summary SDG&E Fixed-Factor Pressure for
Standard Pressure and Temporary Gauge Meter Sets

| SDG&E Fixed Factor Pressure |  |
| --- | --- |
| SDG&E Volume Fixed Factor Pressure | 50,035,048 |
| Estimated SDG&E UAF% Fixed Factor Pressure | 0.10% |
| SDG&E UAF MCF Fixed Factor Pressure | 50,035 |

The allocation of Fixed Factor Pressure gas LUAF is 100% to core customers for both SoCalGas and SDG&E, as non-core customers are equipped with pressure measuring/compensating metering devices.

APPENDIX K

Elevation and Barometric Pressure gas LUAF

Elevation-based LUAF gas results from the elevation where customers actually are served, in the aggregate, being slightly different than the altitude assumed in their billing “altitude zone”.  When the aggregate of customers within a zone (@1000 ft or 400 foot increments) are situated at an altitude below the mean elevation of that zone (used for barometric pressure billing correction) customers on average are under-billed.  When they reside above the elevation zone median, their delivered gas pressure is slightly less gas than assumed and thus a slight over-registration occurs.    An analysis of each of SoCalGas elevation zone was performed in 1991 and discussed in Volume III (Measurement-P. 32) of the 1991 LUAF study.   The associated LUAF results were contained in Tables 3.1.3-3 and 3.1.3-4 of that report.  These results showed that customers were, on-average, situated slightly below their elevation zone mean resulting in higher delivery pressure than assumed.

SoCalGas 2006 data for this component was calculated by applying updated meter and load information for each Altitude Zone where statistical determination of customer elevation was performed in 1991.   SoCalGas performed this update for both customers served at standard pressure and those served at above standard pressure but without site-specific barometric correction.    The results are shown in Tables K-1 and K-2 for standard pressure and above standard pressure customers, respectively.   Standard pressure customers are segregated into eight 1000 foot Altitude zone while above standard pressure customers are segregated into 16 zones of 400 foot increments.

Table K-1 shows the computed gas LUAF contribution of standard pressure meters to be 1,251,906 Mcf.   There was a decrease in 2006 vs. 1991 UAF for Fixed Factor Elevation and Barometric Pressure due to a decrease in the volume delivered through both Standard Pressure and Above Standard Pressure meters using a fixed barometric pressure.  More customers have electronic pressure correctors installed in 2006 than in 1991 and they also have site-specific barometric pressure data programmed into their correction device.

Table K-1

- 2006 UAF Summary Fixed-Factor Altitude Zone for Standard Pressure Meters

| Altitude Zone | Feet Above Sea Level | No. Meters Per Zone | Recorded Volume (MCF) Per Zone | Assumed Altitude Factor For Zone | Apply 1991 Avg % UAF Per Meter In Zone | Total 2006 UAF Volume (MCF) Per Zone |
| --- | --- | --- | --- | --- | --- | --- |
| A | Below 1000 | 4,301,206 | 184,783,983 | 1.000 | 0.52% | 960877 |
| B | 1000 – 1999 | 899,042 | 41,606,532 | 0.968 | 0.73% | 303728 |
| C | 2000 – 2999 | 164,668 | 8,334,536 | 0.935 | -0.23% | -19169 |
| D | 3000 – 3999 | 11,402 | 600,500 | 0.903 | 0.17% | 1021 |
| E | 4000 – 4999 | 12,453 | 685,266 | 0.871 | -0.65% | -4454 |
| F | 5000 – 5999 | 12,678 | 843,134 | 0.841 | 0.00% | 0 |
| G | 6000 – 6999 | 6,191 | 386,451 | 0.812 | 2.44% | 9429 |
| H | 7000 – 7999 | 1,005 | 36,549 | 0.782 | 1.30% | 475 |
|  | 2006 Totals | 5,408,645 | 237,276,951 |  | 0.53% | 1,251,906 |
|  | 1991 Totals | 4,765,459 | 320,392,311 |  |  | 1,695,949 |

Table K-2 shows the 2006 gas LUAF contribution of above standard pressure meters as calculated by integrating the zone bias information from 1991 with 2006 customer data for the same regions.  The result is a gas LUAF reduction of 46,188 Mcf for this set of customers. (They reside, in aggregate, above the mean elevation used for billing within their associated zone, resulting in measurement over-registration.)

Table K-2

- 2006 Fixed-Factor Elevation Zone LUAF for Above Standard Pressure Meters

| Elevation Zone | Feet Above Sea Level | Std Barometric Pressure (psia) | No. Meters Per Zone | 2006 Recorded Volume Per Zone (MCF) | Apply 1991 Avg % UAF Per Meter In Zone | Estimated 2006 UAF Volume Per Zone (MCF) |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | -200 to 199 | 14.73 | 6118 | 56,017,324 | -0.07% | -39,212 |
| 2 | 200 to 599 | 14.53 | 4263 | 35,142,218 | 0.00% | 0 |
| 3 | 600 to 999 | 14.32 | 2580 | 19,647,953 | 0.01% | 1,965 |
| 4 | 1000 to 1399 | 14.12 | 1199 | 16,352,454 | -0.02% | -3,270 |
| 5 | 1400 to 1799 | 13.92 | 478 | 3,787,988 | 0.03% | 1,136 |
| 6 | 1800 to 2199 | 13.72 | 41 | 259,599 | 0.11% | 286 |
| 7 | 2200 to 2599 | 13.53 | 216 | 1,218,916 | -0.12% | -1,463 |
| 8 | 2600 to 2999 | 13.33 | 158 | 6,529,214 | 0.08% | 5,223 |
| 9 | 3000 to 3399 | 13.14 | 22 | 2,514,964 | -0.36% | -9,054 |
| 10 | 3400 to 3799 | 12.96 | 5 | 262,429 | -0.14% | -367 |
| 11 | 3800 to 4199 | 13 | 20 | 153,441 | -0.06% | -92 |
| 12 | 4200 to 4599 | 12.59 | 3 | 5,678 | -0.52% | -30 |
| 13 | 4600 to 4999 | 12.41 | 6 | 7,202 | -0.51% | -37 |
| 14 | 5000 to 5399 | 12.23 | 14 | 433,055 | -0.29% | -1,256 |
| 15 | 5400 to 5799 | 12.06 | 3 | 3,196 | 0.12% | 4 |
| 16 | 5800 to 6199 | 11.89 | 8 | 14,256 | -0.15% | -21 |
| 17 | 6200 to 6599 | 11.72 | 0 | 0 | 0.00% | 0 |
| 18 | 6600 to 6999 | 11.55 | 0 | 0 | 0.00% | 0 |
| 19 | 7000 to 7399 | 11.39 | 0 | 0 | 0.00% | 0 |
|  |  | 2006 Totals | 15,134 | 142,349,887 | -0.03% | -46,188 |
|  |  | 1991 Totals | 15,279 | 413,752,364 | -0.02% | -92,742 |

The total SoCalGas gas LUAF contribution associated with both standard and above standard pressure meters is 1,205,718 Mcf (1,243,910 MMBtu).  Customer class allocation is 100% to core customers, as non-core customers have site-specific barometric pressure correction factors or absolute pressure data integrated into their electronic measurement computation processes, and thus have no part in this LUAF component.

SDG&E:

SDG&E LUAF contribution due to Elevation and Barometric Pressure measurement phenomena for both standard and above standard meters is shown in Table K-3 below to be 194,497 Mcf.  This figure was calculated by applying SoCalGas’ Altitude A and Elevation Zone 1 biases to SDG&E volumes in comparable geographic regions.

Table K-3

| SDG&E Fixed Altitude Zone-standard pressure |  |
| --- | --- |
| SDG&E Volume Fixed Altitude Zone (MCF) | 39,207,013 |
| Est. SDG&E UAF% Fixed Altitude Zone A (Below 1000 ft) | 0.52% |
| SDG&E UAF MCF Fixed Altitude Zone | 203,876 |
| SDGE Fixed Factor Elevation Zone Above Standard Pressure |  |
| SDGE Fixed Factor Elevation Zone Volume (MCF) | 13,398,598 |
| Est. SDGE UAF% Fixed Elevation Zone 1 (SDGE assumes Zone 1) | -0.07% |
| SDGE UAF MCF Fixed Elevation Zone 1 | -9,379 |
| Total SDGE UAF MCF Fixed Factor Altitude & Elevation Zone | 194,497 |

The SDG&E Fixed Factor Elevation gas LUAF contribution customer allocation is 100% to core customers.

APPENDIX L

Fixed Factor Calculation of Super Compressibility

The 1991 Fixed Factor Calculation of Super Compressibility gas LUAF % is shown in 1991 LUAF Measurement report Table 3.1.4-2.  SoCalGas’ 2006 update to this Table, shown in Table L-1, incorporates a measured 2006 average gas temperature of 63.72 degrees F and a much smaller volume of customer volumes subject to this volume due to changes in employed measurement technology.  Another source of improvement is better data used for N2 and CO2 factors for Super compressibility calculation. Electronic Correctors assumed 0% CO2 and N2 in 1991, while values closer to actual gas content in are now incorporated into billing processes.

Year 2006 LUAF% for Super compressibility bias was calculated and applied to the 2006 Volumes for the following two categories of meter sets where Super Compressibility is still calculated using fixed values for Temperature and Gas Quality:  Temporary Gauge and Electronic Corrector-served customers.  The total gas LUAF contribution related to Super compressibility factor bias is shown in Table L-1 to be a LUAF reduction of 44,947 Mcf (46,371 MMBtu).

The large decrease in 2006 vs. 1991 gas LUAF over-registration bias (425,932 vs. 44,947 Mcf) for Fixed Factor Calculation of Super Compressibility was attributable to SoCalGas’ use of actual temperature, pressure and gas quality when calculating corrected volume starting in 1999 for all non-core meters sets except those with Temporary Gauges and Electronic Correctors.  Thus, the volumes subject to super-compressibility calculation bias has decreased substantially.

Table L-1

SoCalGas Fixed Super Compressibility gas LUAF contribution

| Fixed Super Calc Meter Sets | 2006 Billing Volume (MCF) | 2006 Calc’d %UAF | 2006 UAF Volume (Fixed Factor Super Calc) |
| --- | --- | --- | --- |
| Temporary Gauges See Note 1 | 13,671,928 | -0.04% | -4,785 |
| Electronic Correctors See Note 2 | 22,311,895 | -0.18% | -40,161 |
| 2006 Total | 35,983,823 | -0.12% | -44,947 |
| (Actual T 2006 = 63.7) |  |  |  |
| (Billing T 2006 = 60 F) |  |  |  |
| 1991 Totals | 159,387,774 | -0.27% | -425,932 |

Note 1:  Temporary Gauges Billing & Actual Assume SG=0.5918; N2=1.592;CO2=1.507

Note 2:  Electronic Correctors Billing Assumes SG=0.6 and N2=CO2=0.0

Electronic Correctors Actual Assumes same values listed in Note 1.

SDG&E

SDG&E LUAF for this component was calculated by applying SoCalGas calculate bias to SDG&E volumes subject to the same measurement imperfections.  The result, shown in Table L-2, is a gas LUAF reduction of -16,164 Mcf  (16,445 MMBtu) for SDG&E in 2006.

Table L-2

| SDG&E Fixed Factor Super Compressibility |  |
| --- | --- |
| SDG&E Volume Fixed Factor Super Compressibility | 13,469,812 |
| Estimated SDG&E UAF% Fixed Factor Super | -0.12% |
| SDG&E UAF MCF Fixed Factor Super Compressibility | -16,164 |

The allocation of Fixed Factor Super compressibility gas LUAF is 100% to core customers for both SoCalGas and SDG&E, as non-core customers are equipped with gas quality and temperature devices used to calculate real-time compressibility factors.

- APPENDIX M

- 2006 UAF Estimate in Reference to 1991 Assessment

- PD Meter Accuracy

I.	Introduction

PD Meter is the abbreviation for Positive Displacement Meter.  A PD gas meter is a diaphragm-operated or rotary device that is designed to measure a specific volume of gas in one cycle.  These finite volumes are counted and displayed on the meter’s index dials or counters.

PD meters are classified by three major meter groups:

- Small diaphragm meters (up to 500 CFH or Sizes 1, 2 and 3).

- Large diaphragm meters (500 CFH or larger, Size 4 and larger).

- Rotary meters.

The meter accuracy, either under or over volume registration, of all 5.4 million PD meters collectively contributed a significant amount of LUAF in 2006.

II.	PD Meter Accuracy

The accuracy profile is a function of the flow rate.  To assess the consumption behavior of small meter accounts, SoCalGas conducted an extensive study in 1991 to identify the gas consumption volume at various flow rates for Company six weather zones.  The small meter accuracy curves were also developed for a few meter types by using eight flow rates.  The LUAF was derived from the integration of these two sets of data.  Another LUAF contributor – no registration at low flow, was also quantified for small diaphragm meters.

At the same time, the LUAF from the large PD and rotary meters was calculated from 1991 PMC results.  Volume III (Accounting-P.59) of the 1991 LUAF study discusses the PD Meter gas LUAF contribution of 2,957,299 Mcf in that year.

III.	2006 Method for SoCalGas LUAF

The 1991 LUAF study was a major company wide effort in SoCalGas and took two years to complete.  It laid out a format that was used for 2006 assessment.  A benefit from adopting the 1991 format was that many studies completed for the 1991 LUAF assessment were still valid for 2006.  The parameters developed and used in 1991 were used in 2006.  Only certain major factors had to be updated with 2006 data.  The following 1991 parameters were adopted for 2006:

- The consumption volume % vs. flow rates was unchanged.

- The accuracy curve for various flow rates was true because the PD meter technology had not changed since 1991.

- The no registration at low flow was true because of the same reason as (2).

- 2006 Update for SoCalGas LUAF

Similar to the 1991 study, the LUAF contributed by PD meter accuracy was the sum of two parts:

- Small meter low flow non-registration.

- Meter accuracy calculated from the annual Meter Performance Control Program (MPCP) testing results.

To make the assessment comparable to the 1991 results, all PD meters, their annual volume delivery, and MPCP testing results were summarized by major PD meter types.  Then, the same calculation routines used in 1991 were also applied to compute the associated 2006 LUAF volumes.

V.	2006 Results for SoCalGas

- The 2006 LUAF contributed by PD meters is summarized in the following table.

Table M-1

In 1991, the PD meter LUAF was 2,957,299 MCF.  There was some reduction in 2006.  It was due to the meter demographics changes that had occurred in the past 15 years.  The following were observed in the data:

- The tin meter population was reduced from 827,000 in 1991 to 132,000 in 2006.  The tin meter was a positive LUAF contributor.

- Aluminum meters had increased and become the dominant group in the past 15 years.  The population had grown from 2.4 million in 1991 to 4.1 million in 2006.  It was a negative LUAF contributor.

- The large diaphragm meters were decreased and replaced by rotary meters in the last 15 years.  The large diaphragm meters were positive LUAF contributors while rotaries were negative.  However the LUAF of large PD meters was improved in 2006.  It was due to two reasons:

  - Better testing technologies and procedures were developed for rotary meters.

  - Aluminum bodies replaced iron bodies for rotary meters.  It improved the meter accuracy.

VI.	2006 LUAF Assessment for SDG&E

SDG&E has not assessed PD meter LUAF in the past.  There is no format that can be adopted for 2006 update.  To make a logical assessment, the SoCalGas framework was used for 2006.  It is based on the following facts:

- SDG&E uses the same meter technologies as SoCalGas.

- Meters used by SDG&E have the same performance profile as SoCalGas’.

- The consumption behavior of SDG&E’s residential customers is the same as SoCalGas’.

- Table M-2 below shows the results for SDG&E.

Table M-2

The allocation of PD Meter LUAF is virtually 100% to core customers for both SoCalGas and SDG&E based on the 2006 volumes passing though these meters to serve each customer type.

APPENDIX N

- Orifice Meter Accuracy

Orifice meters are used for major customer deliveries, interstate supply, local gas production (supplies) and storage gas measurement.   The 1991 LUAF study Measurement Volume discusses Orifice Meter Accuracy and its LUAF contribution of 5,849,534 Mcf in that year.  The 1991 results are summarized in Table N-1 below.

Table N-1

| Orifice Meter Category | 1991 Volume | 1991 UAF% | 1991 UAF (Mcf) |
| --- | --- | --- | --- |
| Supplier | 963,052,498 | 0.80% | 7,704,420 |
| Producer | 95,527,528 | 0.30% | 286,583 |
| Delivery | 364,526,676 | -0.58% | -2,114,255 |
| Storage Withdrawal | 95,290,197 | 0.33% | 314,458 |
| Storage Injection | 103,536,910 | -0.33% | -341,672 |
| 1991 Totals | 1,621,933,809 | 0.36% | 5,849,534 |

In reviewing the 1991 UAF Study (Table 3.2.2-1 of the Measurement Report) it was determined that 1991 calculated gas LUAF contributions were no longer applicable and should be recalculated for Orifice Meter Accuracy.  Year 2006 supplier and customer orifice meter volumes are 50% less than what they were in 1991.  The reduced volume is now being measured by ultrasonic meters.  In addition, 2 of the 5 sampled supplier orifice meter runs and 11 of the 15 sampled Customer orifice meter runs in the 1991 UAF Study have been removed from service.  Moreover, SoCalGas testing on a removed 12” and 16” Customer Orifice Meter tube in 2006 confirmed that both meters runs under-measured by 0.8% and 0.3% respectively.  2006 Billing Volumes for Customer, Producer, Supplier and Storage Withdrawal and Injection Meters were obtained from MCS.  The 2006 Orifice Meter test results were used to calculate an estimated average orifice meter error for the different categories of orifice meters.  Table N-2 below shows the 2006 contribution to LUAF by meter use category.

Table N-2

2006 Meter Accuracy Contribution to Total Measurement UAF

| Orifice Meter Category | 2006 Volume | Meter Accuracy | UAF % | UAF Volume |
| --- | --- | --- | --- | --- |
| Supplier | 620,936,012 | slow meter | 0.62% | 3,835,149 |
| Producer | 50,799,175 | slow meter | -0.50% | -253,996 |
| Delivery | 115,607,670 | slow meter | 0.50% | 578,038 |
| Storage Withdrawal | 90,112,226 | slow meter | -0.50% | -450,561 |
| Storage Injection | 85,743,196 | slow meter | 0.50% | 428,716 |
| 2006 Totals | 963,198,279 |  | 0.43% | 4,137,346 |

SDG&E:

SDG&E allocations are based on SoCalGas’ test results and SDGE 2006 volumes by meter service.  Table N-3 shows the summary of these calculations and the SDG&E gas LUAF contribution of -26,052 Mcf, a net reduction in LUAF for 2006.

Table N-3

| SDG&E Orifice Meter Accuracy |  |
| --- | --- |
| SDG&E 2006 Orifice Meter Volume Supplier (UAF% = -0.5%) | 5,453,992 |
| SDG&E 2006 Orifice Meter Volume Customers (UAF% = +0.5%) | 243,680 |
| SDG&E 2006 UAF Volume (MCF) Suppliers | -27,270 |
| SDG&E 2006 UAF Volume (MCF) Customers | 1,218 |
| SDG&E 2006 UAF Volume - Orifice Meter Accuracy | -26,052 |

The allocation of orifice meter gas LUAF to customer class was based on calculations which assigned supply volumes to core and non-core by aggregate use, while the Delivery/Customer volumes were assigned exclusively to non-core customers, the only customers served by orifice meters.  The results are SoCalGas non-core - 69.9%, core 30.1%; SDG&E non-core - 57.6%, core 42.4%.

APPENDIX O

Ultrasonic Meter Accuracy

There were no Ultrasonic Meters installed in 1991.  The computation of Ultrasonic meter gas LUAF contribution was completed using the gas LUAF% meter factors shown in Table O-1 below and applying these projected meter registration deviations to 2006 volumes for all company and supplier ultrasonic meters.    The UAF% factors are based on test results and industry information on the types of meters used by SoCalGas and its suppliers.  Table O-1 shows over-registration on both the supply and delivery side for SoCalGas, with the net effect a 205,780 Mcf reduction to LUAF on the SoCalGas system.

Table O-1

| Ultrasonic Meter Category | 2006 Volume | Meter Accuracy | UAF % | UAF Volume |
| --- | --- | --- | --- | --- |
| Supplier (see below) | 275,504,405 | fast meter | 0.22% | 597,867 |
| Delivery - Customer (see below) | 225,360,905 | fast meter | -0.36% | -803,861 |
| Storage W/D Daniel Mtr PDR | 3,270,934 | fast meter | 0.13% | 4,252 |
| Storage Injection Daniel Mtr PDR | 3,106,221 | fast meter | -0.13% | -4,038 |
| 2006 Totals | 507,242,465 |  | -0.04% | -205,780 |

SDG&E:

SDG&E Ultrasonic meter LUAF contribution is based on a SoCalGas test results, specific meter activity and SDGE 2006 volumes by meter service. Table O-2 shows the summary of these calculations and the SDG&E gas LUAF contribution of 509,059 Mcf in 2006.

Table O-2

| SDG&E Ultrasonic Meter Data |  |
| --- | --- |
| SDG&E 2006 Ultrasonic Meter Volume Supplier (Mcf) | 113,952,358 |
| SDG&E 2006 Ultrasonic Meter Volume Customer (Mcf ) | 30,351,489 |
| SGG&E Ultrasonic Meter LUAF Contribution |  |
| SDG&E 2006 UAF Volume (MCF) Suppliers (UAF% = +0.5%) | 569,762 |
| SDG&E 2006 UAF Volume (MCF) Customers (UAF% = -0.2%) | -60,703 |
| SDG&E 2006 UAF Volume Contribution from Ultrasonic Meters-total | 509,059 |

The 2006 allocation of ultrasonic meter gas LUAF to customer class is based on calculations which assigned supply volumes to core and non-core by aggregate use, while the Delivery/Customer volumes were assigned exclusively to non-core customers, the only customers served by ultrasonic meters.  The results are SoCalGas - non-core -441,216 MMBtu (credit) due to over registration, core - 228,963 MMBtu LUAF contribution.  SDG&E non-core - 232,171 MMBtu, core 285,739, both LUAF contributions.

APPENDIX P

Turbine Meter Accuracy

Turbine meters are used by both companies to serve mainly non-core customers.  Volume III (Accounting-P.99) of the 1991 LUAF study discusses Turbine Meter Accuracy and its LUAF contribution of -912,157 Mcf in that year.  As in 1991, this gas LUAF component is based on the results of lab calibration tests for meters removed from service and includes field calibration (Aux factors) which now places the lab calibration bias number in the field devices to provide true zero meter registration upon installation. Table P-1 below shows the results of turbine meter tests in 2006 to average 0.39% over registration across the different types of meters.   Overall these results show a slight increase from 1991.

Table P-1

2006 and 1991 LUAF factors for turbine meters from test data

Table P-2 below shows the integration and application of individual turbine meter species’ test results to the SoCalGas customer volumes associated with these meter types.  The net result is a volume-weighted 0.28% over registration for all turbine meter volumes. This equates to 797,839 in over registration and associated reduction in LUAF.

Table P-2

2006 Gas LUAF for SoCalGas Turbine meters by type.

SoCalGas Sample Meter Volumes Meter Type

Recorded

Volume

(MSCF)

UAF

Volume

(MCF)

UAF Factor

Recorded

Volume

MSCF

UAF

Volume

(MSCF)

AAT-18

14,726,622

(22,515)

-0.15%

41,271,763

(63,100)

AAT-30

7,630,933

(21,877)

-0.29%

39,880,742

(114,335)

AAT-60

10,771,986

(11,639)

-0.11%

37,532,194

(40,554)

AAT-140

9,250,414

(63,970)

-0.69%

81,176,600

(561,367)

Other Types

-0.28%

6,600,752

(18,482)

Totals:

42,379,955

(120,002)

206,462,051

(797,839)

Average Sample UAF Factor =

-0.28%

Average System UAF Factor =

-0.39%

1991

Average System UAF Factor =

-0.34%

2006 Sample Meters

Total 2006 System

SDG&E:

San Diego Gas & Electric’s turbine meter associated LUAF was based on a similar methodology to SoCal Gas and also compensated for the fact that SDG&E does not include a meter aux factor in its field configuration. Table P-3 shows the result of 73,178 Mcf over-registration based on SDGE meter test results of 0.23% over-registration.  This bias was applied to SDG&E 2006 turbine meter volumes.

Table P3

SDG&E Sample Meter Volumes

Recorded

Volume

(MSCF)

UAF

Volume

(MCF)

UAF Factor

Recorded

Volume

MSCF

UAF

Volume

(MSCF)

Totals:

42,403,990

(95,967)

32,334,490

(73,178))

Average Sample UAF Factor =

-0.23%

Average System UAF Factor =

-0.23%

2006 Sample Meters

Total 2006 System

The allocation of Turbine Meter gas LUAF is 97.33% to non-core for SoCalGas and 96.69% to non-core for SDG&E based on turbine meter volumes per core vs. non-core customers.  Nearly all turbine meters serve non-core customers in both companies.

APPENDIX Q

Instrument Calibration Bias Gas LUAF Component

Electronic instruments are used on approximately 10,000 SoCalGas customer accounts to correct for temperature, pressure and/or gas quality.  The calibration of these devices can shift between scheduled calibration periods.  Instrument Calibration Bias gas LUAF contribution is calculated from actual field audits performed in 2006 (using “as-found” data) for customer, supplier and storage meters where electronic correction is performed, and now includes the sub-component Ambient Temperature Effect on Instrumentation.

Table Q-1 shows the result of SoCalGas’ calibration as-found results by major instrument type in 2006.  This table also contains the volumes served by these instruments and the calculated contribution to LUAF in 2006.  The SoCalGas total is -261,961 Mcf, a net LUAF reduction.

Table Q-1

Customer Other than orifice and ultrasonic:				           error%

| Temporary Gauges | 15,486,336 | -2,113 | -0.01% |
| --- | --- | --- | --- |
| MINI-AT | 82,152,739 | 99,424 | 0.12% |
| ECAT | 42,501,793 | -44,167 | -0.10% |
| TOC | 52,022,099 | -9,403 | -0.02% |
| OMNI | 72,462,221 | 31,254 | 0.04% |
| Totalflow | 58,766,964 | -4,923 | -0.01% |
| GM | 2,700,154 | -2,713 | -0.10% |
| Subtotal | 326,092,307 | 67,359 | 0.03% |
| Ultrasonic Meters |  |  |  |
| Supplier | 275,504,405 | -118,828 | -0.04% |
| Customer | 225,360,904 | 97,200 | 0.04% |
| Subtotal | 500,865,309 | -21,627 | 0.00% |
| Orifice Meters |  |  |  |
| Supplier | 620,936,012 | -335,325 | -0.05% |
| Producer | 50,799,175 | -27,433 | -0.05% |
| Customer | 115,607,670 | 62,432 | 0.05% |
| Subtotal | 787,342,857 | -300,326 | -0.04% |
| Ultrasonic Meters |  |  |  |
| Injection | 3,106,221 | -1,340 | -0.04% |
| Withdrawal/Injection | 3,270,934 | 1,411 | 0.04% |
| Subtotal | 6,377,155 | 71 | 0.00% |

| Orifice Meters |  |  |  |
| --- | --- | --- | --- |
| Injection | 85,743,196 | -46,304 | -0.05% |
| Withdrawal/Injection | 90,112,226 | 38,866 | 0.05% |
| Subtotal | 175,855,422 | -7,438 | 0.00% |
| Total | 1,796,533,050 | 261,961 | Wt Avg 0.015% |

The SoCalGas allocation is 99% to the non-core customer class based on weighted delivered volume considerations.  Core allocation is 1%.

SDG&E:

SoCalGas’ average recorded instrument error of 0.015% (over-registration) was applied to associated SDG&E customer and supply meters to compute the 2006 Instrument Bias gas LUAF component for SDG&E.  There are many similar electronic instruments used between the companies.  The results are shown in the Table Q-2 below to be an 11,325 Mcf reduction to gas LUAF.  The allocation is 89% to the non-core customer class based on weighted volume considerations.  Core allocation is 11%.

Table Q-2

SDGE instrument bias

APPENDIX R

Ambient Temperature Effect on Instrumentation

Ambient Temperature Effect on Instrumentation – Ambient temperature effect is now included in the subcomponent “Instrument Calibration Bias” for both companies.

APPENDIX S

Chart Integration Bias

Measurement pen chart technology has been replaced by electronic measurement for both SoCalGas and SDG&E since 1991.  There is no 2006 measurement component for either company.

APPENDIX T/U

Distribution and Transmission Leakage

This Appendix contains the results for both Distribution and Transmission gas LUAF leakage calculations for SoCalGas and SDG&E in 2006.   This is leakage resulting from pipeline gas escape and gas blow-by events from gas compression operations which are otherwise neither metered nor form-reported  for inclusion as “Company Use” in SDG&E's and SoCalGas' accounting systems.

Raw Data Sets for Distribution and Transmission and distribution pipeline leak contribution to gas LUAF are shown in Table T/U-1.

Table T/U-1

SoCalGas/SDG&E Base Leak data and volumetric LUAF contribution.

Updated 2006 calculations for leakage associate with compressor station operation for both SDG&E and SoCalGas are show in Table T/U-2.  This Table shows the 2006 run hours for each station and the hourly leak factors used to calculate leakage for each company.  The results show the SoCalGas gas LUAF contribution to be 20,789 Mcf from compressor station operation, while the SDG&E sub-component is 1129 Mcf.

Table T/U-2

Compressor Station 2006 Leak Contributions to LUAF in MCF- SoCalGas and SDG&E

Table T/U-3 shows the 2006 compilation results for Transmission and Distribution leakage for both SDG&E and SoCalGas.  The SoCalGas Distribution leak total (566,861 Mcf) is taken directly from a Gas Engineering report using updated 2006 pipeline leakage data.   SDG&E distribution leakage was computed by scaling the SoCalGas result using relative distribution pipeline mileage between the two companies.  The SDG&E 2006 result for distribution leakage gas LUAF contribution is 99,378 Mcf.

The total Transmission Leak gas LUAF component is the sum of compressor station leakage and computed transmission line leakage for each company.   The totals are shown below under items 3 and 4 as 29,755 Mcf for SoCalGas and 2,948 Mcf for SDG&E.

Table T/U-3

Allocation of system leak gas LUAF contribution to customer class is based on which pipelines are used to serve customers on a volume-weighted basis.  Transmission leakage is a component fully shared by core and non-core customer classes based on the ratio of delivered energy to these customer classes (every customer essentially uses transmission lines.)   The allocations for transmission leakage are SDG&E: core- 40.55%, non-core 59.55%; SoCalGas: core - 37.1%, non-core -  62.9%.

Distribution leak allocation is based on the proportion of customer volumes which are served via distribution lines.  All core customers and a subset of non-core customers are served by distribution pipelines.   The allocation for distribution leakage is 76.48% core and 23.52% non-core for both companies.

APPENDIX V

Theft

Two calculation methods were used in the 1991 study and the method with the larger amount of LUAF was chosen.  After updating these calculations for customer growth and other factors, an average of the two calculation methods was used for this revision resulting in a slight decrease in the percentage of this sub-component.  This component was estimated for SDG&E based on SoCalGas’ proportion of LUAF for the same category using SDG&E volumes.  Table V-1 below shows the SoCalGas result to be 397,288 Mcf while Table V-2 shows the SDGE component to be 54,134 Mcf.

Table V-1

SDG&E Theft Calculation Sheet

|  | Residential |  | Non-Residential |  |
| --- | --- | --- | --- | --- |
|  | 1991 | 2006 | 1991 | 2006 |
| Customers | 4,430,000 | 5,367,739 | 218,669 | 268,556 |
| customers who steal | 3,207 | 3,886 | 592 | 728 |
| % customers who steal | 0.072% | 0.072% | 0.271% | 0.271% |
| Ave Gas Stolen/convicted cust | 71.4 | 69.24 | 333.3 | 176.23 |
| Total Stolen MCF | 228,980 | 269,067 | 197,460 | 128,221 |
| Percent of Total | 54% | 68% | 46% | 32% |
| 2006 Total Stolen MCF | 397,288 |  |  |  |

Table V-2

SDG&E Theft Calculation Sheet

|  | Residential |  | Non-Residential |  |
| --- | --- | --- | --- | --- |
|  | SoCal | SD | SoCal | SD |
|  | 1991 | 2006 | 1991 | 2006 |
| Customers | 4,430,000 | 802,140 | 218,669 | 29,167 |
| customers who steal | 3,207 | 581 | 592 | 79 |
| % customers who steal | 0.072% | 0.072% | 0.271% | 0.271% |
| Ave Gas Stolen/convicted cust | 71.4 | 69.24 | 333.3 | 176.23 |
| Total Stolen MCF | 228,980 | 40,209 | 197,460 | 13,926 |
| Percent of Total | 54% | 74% | 46% | 26% |
| Total Stolen MCF | 54,134 |  |  |  |

Residential theft was assigned to core market while non-residential theft has been allocated to non-core customers for both companies.  The results are:  SoCalGas Core - 68%, non-core 32%; SDG&E core 74%, non-core 26%.

APPENDIX W

Intentionally left Blank

APPENDIX 2:  Annual Data--Summary Data

/ 	California Public Utilities Commission, Opinion Adopting Market Price Referent Methodology D.05-12-042 http://www.cpuc.ca.gov/WORD_PDF/FINAL_DECISION/52178.PDF (12/19/2005).

/ 	New York Mercantile Exchange. NYMEX ClearPort(sm) Clearing and NYMEX ClearPort(sm) Trading Contract Settlements https://www.services.nymex.com/otcsettlement/OTCSettle.jsp.