## OH Drop
OH Voltage Drop Calculation
CASE :
[6 empty] | S1 |  |  |  | OH Transformer Impedances
| L1 | L2 L3 | L4 L5 | L6 L7 | L8 L9 L10 |  |  | Line AMPS | % Load | Size | % R | %X | SINGLE PHASE & OPEN DELTA
[8 empty] | 162.037 | 77.78% | 10 | 1.4 | 1.1 | CLOSE DELTA & Y
[10 empty] | 15 | 1.3 | 1.3
[8 empty] | V Drop | % V Drop | 25 | 1.1 | 1.4
| 1-PH = 1 | System | L-L Voltage | Power Factor | Angle |  |  | 3.1446 | 1.3102 | 50 | 1 | 1.8
| 3-PH = 3 | 1 | 240 | 0.9 | 25.8419 |  |  |  |  | 75 | 0.9 | 1.9
Overhead Transformer | [9 empty] | 100 | 1 | 2.1
KVA | Load in AMPS | Load in KW | % Load | %R | %X | V Drop | % V Drop
50 | 0 | 35 | 77.78% | 1 | 1.8 | 3.1446 | 1.3102
Secondary and Services
Load Point | Wire Size | Length in Feet | No of Runs | Load in AMPS | Load in KW | V Drop | % V Drop | Line AMPS | Z XARM | V Drop | % V Drop
L1 |  | 0 | 0 | 0 | 24 | 0 | 0 | 111.1111 | 0
L2 |  | 0 | 0 | 0 | 16 | 0 | 0 | 74.0741 | 0
L3 |  | 0 | 0 | 0 | 10 | 0 | 0 | 46.2963 | 0
L4 |  | 0 | 0 | 0 | 6 | 0 | 0 | 27.7778 | 0
L5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A
L6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
L7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
L8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
L9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
L10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A
S1 |  | 0 | 0 | 0 | 3 | 0 | 0 | 13.8889 | 0
[5 empty] | Subtotal | 0 | 0
Note: See Conductor Data for available wire sIzes
|  |  |  | Total Voltage Drop |  | 3.1446 | 1.3102
Conductor Data
Main Menu
Exit
Print
Flicker
Diversity Factors

## Volt Drop Doc
VOLTAGE DROP CALCULATION CASE STUDY
Steady State
|  |  | Customer in the case study |  |  | S1
CASE : | CUSTOMER ADDRESS |  |  |  | Service
| L1 | L2 L3 | L4 L5 | L6 L7 | L8 L9 L10
Secondary
Instructions
1 - Input customer address for case study.
2 - Input system type : (1 for single phase, or 3 for three phase)
3 - Input secondary line to line voltage.
4 - Input transformer size in KVA.
5 - Input diversified load in KW or AMPS for entire secondary system
fed by transformer. This is the total transformer load.
6 - Input diversified load in KW or AMPS across each secondary
segment labeled L1 - L10 as applicable.
7 - Input load in KW or AMPS for service in the case study labeled S1.
8 - Input proper conductor type and size for each secondary segment
and service. Click on the Conductors Macro Button for available
conductor types and sizes. Copy and paste appropriate conductor data.
9 - Input proper length in feet and number of runs for each segment
and service as needed.
Notes : Input in KW cells override input in AMPS, zero KW cells if input is in AMPS.
Total voltage drop includes drop accross transformer, secondary, and service.
Transformer
Main Menu
OH Drop
UG Drop
Exit
Print

## Demand
Demand Estimating DM 5322
Dwelling Type | KW Demand Categories |  |  | Diversity Factors
| SQ. Ft. | Base Load | Air Cond. | Residential
Single Family Attached | 0 - 1299 | 3.0 | 5.0 | # Customers | Base Load
| 1300 - 1999 | 4.0 | 6.0 | 1 - 2 | 1.0
| 2000 - 2999 | 4.5 | 7.0 | 3 - 4 | 0.75
Single Family Attached | 0 - 1299 | 3.0 | 4.0 | 5 - 7 | 0.65
| 1300 - 1999 | 4.0 | 5.0 | 8 - 14 | 0.55
| 2000 - 2999 | 4.5 | 5.5 | => 15 | 0.50
Multi-Family Apartments | 0 - 1299 | 1.5 | 3.5 | Commercial
| 1300 - 1999 | 2.0 | 4.0 | 1 | 1.0
Mobile Homes | 0 - 1299 | 2.5 | 5.0 | 2 | 0.90
| 1300 - 1999 | 3.0 | 6.0 | 3 | 0.80
|  |  |  | 4 | 0.70
Print
OH Drop
UG Drop
Main Menu
Exit

## OH Flicker
OH Flicker Calculation
CASE : | 2962-2968 E st alley
[6 empty] | S1 |  |  |  | OH Transformer Impedances
| L1 | L2 L3 | L4 L5 | L6 L7 | L8 L9 L10 |  |  | Line AMPS | % Load | Size | % R | %X | SINGLE PHASE & OPEN DELTA
[8 empty] | 103 | 49.44% | 10 | 1.4 | 1.1 | CLOSE DELTA & Y
[10 empty] | 15 | 1.3 | 1.3
[8 empty] | V Drop | % V Drop | 25 | 1.1 | 1.4
1-PH = 1 | System | L-L Voltage | MOTOR HP | LRC AMP | Power Factor | Angle | Total Flicker | 2.3984 | 0.99934 | 50 | 1 | 1.8
3-PH = 3 | 1 | 240 |  | 103 | 0.31 | 71.9408 | % Allowed |  |  | 75 | 0.9 | 1.9
Overhead Transformer | [9 empty] | 100 | 1 | 2.1
KVA | LRC AMP | % Load | %R | %X | V Drop | % Flicker
50 | 103 | 49.44% | 1 | 1.8 | 2.3984 | 0.99934
Secondary and Services | [6 empty] | Cumulative
Load Point | Wire Size | Length in Feet | No of Runs | LRC AMP | V Drop | % Flicker | % Flicker | Line AMPS | Z XARM | V Drop | % V Drop
L1 | 3/0 USA | 70 | 1 | 103 | 1.9479 | 0.81162 | 1.811 | 103 | 0.13508 | 1.9479 | 0.81162
L2 | 3/0 USA | 85 | 1 | 103 | 2.3653 | 0.98554 | 2.7965 | 103 | 0.13508 | 2.3653 | 0.98554
L3 | 3/0 USA | 40 | 1 | 103 | 1.1131 | 0.46378 | 3.2603 | 103 | 0.13508 | 1.1131 | 0.46378
L4 | 1/0 USA | 92 | 1 | 103 | 3.8704 | 1.6127 | 4.873 | 103 | 0.20422 | 3.8704 | 1.6127
L5 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | #N/A
L6 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
L7 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
L8 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
L9 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
L10 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | #N/A
S1 | 1/0 USA | 44 | 1 | 103 | 1.8511 | 0.77128 | 5.6442 | 103 | 0.20422 | 1.8511 | 0.77128
[5 empty] | 11.1477 | 4.6449
Note: See Conductor Data for available wire sizes
[5 empty] | 13.5461 | 5.6442
Conductor Data
Main Menu
Exit
Print
OH drop
Motor Data
Flicker Limits

## UG Drop
UG Voltage Drop Calculation
CASE :
S1
| L1 | L2 L3 | L4 L5 | L6 L7 | L8 L9 L10 |  |  | Line AMPS | % Load | %R | %X
[8 empty] | 186.531 | 89.53% | 1.1 | 1.8
[8 empty] | V Drop | % V Drop
| 1-PH = 1 | System | L-L Voltage | Power Factor | Angle |  |  | 4.0066 | 1.6694
| 3-PH = 3 | 1 | 240 | 0.86 | 30.6834
Underground Transformer
KVA | Load in AMPS | Load in KW | % Load | %R | %X | V Drop | % V Drop
50 | 0 | 38.5 | 89.53% | 1.1 | 1.8 | 4.0066 | 1.6694
Secondary and Services | [11 empty] | OH Transformer Impedances
Load Point | Wire Size | Length in Feet | No of Runs | Load in AMPS | Load in KW | V Drop | % V Drop | Line AMPS | Z XARM | V Drop | % V Drop | Size | % R | %X | SINGLE PHASE & OPEN DELTA
L1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 25 | 1.2 | 1.5 | SINGLE PHASE & OPEN DELTA
L2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 50 | 1.1 | 1.8 | SINGLE PHASE & OPEN DELTA
L3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 75 | 0.9 | 1.8 | SINGLE PHASE & OPEN DELTA
L4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 100 | 0.9 | 1.9 | SINGLE PHASE & OPEN DELTA
L5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | [5 empty] | SINGLE PHASE & OPEN DELTA
L6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Size | % R | %X
L7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 75 | 1 | 3.2 | CLOSE DELTA
L8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 100 | 1 | 1.9 | THREE PHASE PAD MOUNTED
L9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 150 | 1 | 3.2 | THREE PHASE PAD MOUNTED
L10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A |  |  | 225 | 0.9 | 3.6 | THREE PHASE PAD MOUNTED
S1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 300 | 0.8 | 3.9 | THREE PHASE PAD MOUNTED
[5 empty] | Subtotal | 0 | 0 |  |  |  |  | 500 | 0.7 | 4.4 | THREE PHASE PAD MOUNTED
Note: See Conductor Data for available wire sizes | [11 empty] | 750 | 0.8 | 5.7 | THREE PHASE PAD MOUNTED
|  |  |  | Total Voltage Drop |  | 4.0066 | 1.6694 |  |  |  |  | 1000 | 0.7 | 5.6 | THREE PHASE PAD MOUNTED
Conductor Data
Main Menu
Exit
Flicker
Print
Diversity Factors

## UG Flicker
UG Flicker Calculation
CASE :
S1
| L1 | L2 L3 | L4 L5 | L6 L7 | L8 L9 L10 |  |  | Line AMPS | % Load | %R | %X
[8 empty] | 103 | 49.44% | 1.1 | 1.8
[8 empty] | V Drop | % V Drop
1-PH = 1 | System | L-L Voltage | Motor HP | LRC AMP | Power Factor | Angle | Total Flicker | 2.429 | 1.0121
3-PH = 3 | 1 | 240 | 0 | 103 | 0.3 | 72.5424 | % Allowed
Underground Transformer | [6 empty] | 2
KVA | LRC AMP | % Load | %R | %X | V Drop | % Flicker
50 | 103 | 49.44% | 1.1 | 1.8 | 2.429 | 1.0121
Secondary and Services | [6 empty] | Cumulative |  |  |  |  | UG Transformer Impedances
Load Point | Wire Size | Length in Feet | No of Runs | LRC AMP | V Drop | % Flicker | Flicker | Line AMPS | Z XARM | V Drop | % V Drop | Size | % R | %X | SINGLE PHASE & OPEN DELTA
L1 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | #N/A |  |  | 25 | 1.2 | 1.5 | SINGLE PHASE & OPEN DELTA
L2 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | #N/A |  |  | 50 | 1.1 | 1.8 | SINGLE PHASE & OPEN DELTA
L3 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | #N/A |  |  | 75 | 0.9 | 1.8 | SINGLE PHASE & OPEN DELTA
L4 |  | 92 | 0 | 0 | 0 | 0 | 1.0121 | 0 | #N/A |  |  | 100 | 0.9 | 1.9 | SINGLE PHASE & OPEN DELTA
L5 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | #N/A | [5 empty] | SINGLE PHASE & OPEN DELTA
L6 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | Size | % R | %X
L7 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 75 | 1 | 3.2 | CLOSE DELTA
L8 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 100 | 1 | 1.9 | THREE PHASE PAD MOUNTED
L9 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 150 | 1 | 3.2 | THREE PHASE PAD MOUNTED
L10 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | #N/A |  |  | 225 | 0.9 | 3.6 | THREE PHASE PAD MOUNTED
S1 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 300 | 0.8 | 3.9 | THREE PHASE PAD MOUNTED
|  |  |  | Subtotal | 0 | 0 | [5 empty] | 500 | 0.7 | 4.4 | THREE PHASE PAD MOUNTED
Note: See Conductor Data for available wire sIzes | [11 empty] | 750 | 0.8 | 5.7 | THREE PHASE PAD MOUNTED
|  |  |  | Total | 2.429 | 1.0121 | [5 empty] | 1000 | 0.7 | 5.6 | THREE PHASE PAD MOUNTED
Conductor Data
Main Menu
Exit
UG Drop
Print
Motor Data
Flicker Limits

## Flicker Doc
FLICKER CALCULATION CASE STUDY
Steady State
|  |  | Customer in the case study |  |  | S1
CASE : | CUSTOMER ADDRESS |  |  |  | Service
| L1 | L2 L3 | L4 L5 | L6 L7 | L8 L9 L10
Secondary
Instructions
1 - Input customer address for case study.
2 - Input system type : (1 for single phase, or 3 for three phase)
3 - Input secondary line to line voltage.
4 - Input Motor size in HP, LRC in AMPS, and Power Factor. If starting
current and Power Factor are not available, click on the Motor Data
Macro Button for recommended values.
5 - Input maximim allowed percent flicker for the case study. Click on the
Flicker limits Macro Button for designated Limits.
6 - Input transformer size in KVA.
7 - Input LRC AMPS through the transformer secondary.
8 - Input LRC AMPS across each secondary segment (L1-L10) and service (S1).
9 - Input proper conductor type and size for each secondary segment
and service. Click on the Conductors Macro Button for available
conductor types and sizes. Copy and paste appropriate conductor data.
10 - Input proper length in feet and number of runs for each segment and service.
NOTES:
Total percent flicker includes contributions by transformer, secondary, and service.
Transformer
Main Menu
OH Flicker
UG Flicker
Exit
Print

## Downsizing
TRANSFORMER DOWNSIZING STUDY
Last Service (Longest secondary and service)
S1
CASE : | STATION NUMBER |  |  |  | Service
| L1 | L2 L3 | L4 L5 | L6 L7 | L8 L9 L10
Secondary
Instructions
1 - Obtain TLM file to determine number of customers served.
2 - Review demand history for at least one year to confirm transformer eligibility.
3 - Determine most appropriate recording period to capture peak demand.
4 - Record voltage and current for a minimum of three days (preferably 7 days).
5 - Obtain wire / conductor size and length information for all secondaries
and services. (Could be done when installing recorder).
6 - Check recording results for presence of inrush currents from elevator motors
and compressors.
7 - Determine allowable % flicker for load type (residential, commercial, industrial).
8 - Verify existing flicker and voltage drop conditions through software calculations.
9 - Conduct complete voltage drop and flicker calculations for various transformers
to determine optimum transformer size.
10 - Perform a PVARR calculation to determine least cost option.
Transformer
Main Menu
Flicker Limits
Exit
Print

## Conductors
CONDUCTOR DATA FOR USE WITH VOLTAGE AND FLICKER CALCULATION
Overhead | Underground
Size /Type | Size /Type
1/0 AER | 1/0 USA
1/0 BS CU | 1000 USA
1/0 SSC AL | 2 USA
1/0 THW CU | 3/0 USA
1/0 WP AL | 350 USA
1/0 WP CU | 4/0 THW CU-UG
2 BS CU | 500 THW CU-UG
2 SSC AL | 500 USA
2 SSC CU
2 THW CU
2 WP AL
2 WP CU
3/0 AER
3/0 SSC AL
3/0 WP AL
336 WP AL | Available Conductors and Wires
336 AER
4 BS CU | Copy and paste conductor / wire sizes
4 SSC AL | as needed for voltage and flicker calculations
4 SSC CU
4 THW CU
4 WP AL
4 WP CU
4/0 THW CU
500 THW CU
6 BS CU
6 SSC CU
6 THW CU
6 WP AL
6 WP CU
Main Menu
OH Drop
OH Flicker Menu
UG Drop
UG Flicker Menu
OH Wire Ampacities
UG Cable Ampacities
Print
Transformer Loading

## UG Cable Ampacities
UNDERGROUND C A B L E A M P A C I T I E S
600 VOLT SECONDARY ALUMINUM CABLE, DB CONDUIT, TOTAL AMPACITY FOR EACH PHASE
7-1/2 INCHES CENTERLINE TO CENTERLINE SPACING BETWEEN CONDUITS
CABLE | CONDUIT | # OF | NUMBER OF RUNS
SIZE | SIZE | COND. | 1 | 2 | 3 | 4 | 5 | 6 | 7
1000 | 5" | 3-1/C | 605 | 1104 | 1527 | 1892 | 2335 | 2526 | 2821
500 | 4" | 3-1/C | 397 | 736 | 1029 | 1288 | 1595 | 1746 | 1953
350 | 3" | 2-1/C | 318 | 600 | 852 | 1076 | 1285 | 1482 | 1673
350 | 3" | 3-1/C | 313 | 586 | 822 | 1036 | 1230 | 1416 | 1589
3/0 | 2" | 2-1/C | 202 | 386 | 552 | 704 | 875 | 984 | 1113
3/0 | 3" | 3-1/C | 199 | 376 | 534 | 676 | 810 | 936 | 1057
1/0 | 2" | 2-1/C | 152 | 292 | 420 | 536 | 645 | 750 | 854
#2 | 2" | 2-1/C | 113 | 218 | 315 | 404 | 490 | 570 | 651
#8 | 1" | 1/C | 47 | 92 | 135 | 176 | 215 | 252 | 287
WITHOUT 7-1/2" CENTERLINE TO CENTERLINE BETWEEN CONDUITS
CABLE | CONDUIT | # OF | NUMBER OF RUNS
SIZE | SIZE | COND. | 1 | 2 | 3 | 4
1000 | 5" | 3-1/C | N/A | 1092 | 1476 | 1848
500 | 4" | 3-1/C | N/A | 724 | 996 | 1244
350 | 3" | 2-1/C | N/A | 588 | 816 | 1036
350 | 3" | 3-1/C | N/A | 572 | 789 | 992
3/0 | 2" | 2-1/C | N/A | 376 | 531 | 664
3/0 | 3" | 3-1/C | N/A | 370 | 516 | 644
1/0 | 2" | 2-1/C | N/A | 287 | 405 | 506
#2 | 2" | 2-1/C | N/A | 214 | 303 | 384
#8 | 1" | 1/C | N/A | 92 | 132 | 168
Print
Main Menu
UG Drop
UG Flicker
Conductors

## OH Cable Ampacities
OVERHEAD C A B L E A M P A C I T I E S
600 VOLT SECONDARY ALUMINUM AND COPPER WIRE, TOTAL AMPACITY FOR EACH PHASE
COPPER
CABLE | BARE | BARE | THW |  | POLY INSL |  | TREE | WP
SIZE | SOL | STRD | 3 C | 1-AIR | TRIPLX | QUAD | WIRE | SOL | STRD
12 |  |  | 20 | 25
10 |  |  | 30 | 40
8 | 90 |  | 45 | 65 | 70 |  |  | 71
6 | 120 | 130 | 65 | 96 | 100 | 80 |  | 96
4 | 170 | 180 | 85 | 125 | 135 | 120 | 125 | 128
2 |  | 230 | 115 | 170 | 180 |  | 166 |  | 176
1 |  | 270
1/0 |  | 310 | 150 | 230 |  |  | 222 |  | 243
2/0 |  | 360 | 175 | 265 |  |  |  |  | 282
3/0 |  |  | 200 | 310 |  |  | 294
4/0 |  | 480 | 230 | 360 |  |  | 343 |  | 387
250 |  | 540 | 255 | 405
300 |  |  | 285 | 445
350 |  |  | 310 | 505
400 |  | 730 | 335 | 545
500 |  | 840 | 380 | 620 |  |  |  |  | 684
750 |  | 1090 | 475 | 785 |  |  |  |  | 871
1000 |  | 1300 | 545 | 935 |  |  |  |  | 1055
ALUMINUM
CABLE | ACSR | RTS | SSC | SSC | POLY
SIZE | BARE | BARE | TRIPX | QUAD | INSL
4 | 140 |  | 100 |  | 125
2 | 180 |  | 135 | 112 | 170
1/0 | 230 | 180 | 180 |  | 230
3/0 | 300 | 250 |  | 192 | 310
4/0 | 340
336 | 530 | 400 |  |  | 480
397 | 590
636 | 780
1033 | 1060
Print
Main Menu
OH Drop
OH Flicker Menu
Conductor Data

## Motor Data
Lock Rotor Currents DM 5413
STARTING MOTOR CURRENTS LRC
Motor Size in HP | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200
1-PH 120 V | 45 | 69 | 92
1-PH 240 V | 27 | 34 | 46 | 69 | 103 | 115 | 138 | 163 | 218
3-PH 208 V |  |  |  | 69 | 92 | 100 | 113 | 131 | 161 | 230 | 308 | 380 | 456 | 608 | 770 | 1159 | 1546 | 2319 | 3092 | 3-PH 208 V
3-PH 240 V |  |  |  | 60 | 80 | 87 | 98 | 115 | 141 | 201 | 268 | 335 | 402 | 536 | 670 | 1005 | 1340 | 2010 |  | 3-PH 240 V
3-PH 480 V |  |  |  | 30 | 40 | 43 | 49 | 58 | 71 | 100 | 134 | 168 | 201 | 268 | 335 | 503 | 670 | 1005 | 1340 | 3-PH 480 V
POWER FACTOR
1. USE THE NAME PLATE POWER FACTOR.
2. IF NOT AVAILABLE, SELECT THE VALUE FROM THE FOLLOWING TABLE:
Motor HP | 1 - 25 | 30 | 40 | 50 | 60 | 75 | 100 | 150 | 200 | 250 | 300 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1200 | 1500
Power Factor | 0.3 | 0.419 | 0.39 | 0.382 | 0.349 | 0.33 | 0.309 | 0.28 | 0.251 | 0.231 | 0.219 | 0.199 | 0.178 | 0.167 | 0.167 | 0.167 | 0.161 | 0.148 | 0.148 | 0.148
OH Flicker
UG Flicker
Main Menu
Flicker Limits
Print

## Flicker
Secondary Flicker Limits DM5413
EQ | Frequency Fluctuations |  |  |  | %
Type | Day | Hour | Minute | Second | Flicker | 1 - House Pumps, Compressors, AC Units
1 | 10 - 30 |  |  |  | 6% | 2 - Single Elevators, Hoists, X-Ray Equipment
|  | 1 - 5 |  |  | 6% | 3 - Group Elevators, Saws, Spot Welders
|  | 5 - 30 |  |  | 5% | 4 - Automatic Spot Welders
2 |  |  | 1 - 10 |  | 2.5%
3 |  |  | 10 - 30 |  | 2%
4 |  |  |  | 1 - 1.75 | 2%
|  |  |  | 1.75 - 30 | 1%
Main Menu
Motor Data
OH Flicker
UG Flicker
Print

## Transformer Loading
TRANSFORMER FULL LOAD CURRENT IN AMPERES AT RATED LINE VOLTAGE
SINGLE PHASE - LINE CURRENTS
KVA | RATED LINE VOLTAGE
RATING | 120 | 240 | 480 | 2400 | 4160 | 6930 | 7200 | 12000 | 12470
10 | 83.3333 | 41.6667 | 20.8333 | 4.1667 | 2.4038 | 1.443 | 1.3889 | 0.83333 | 0.80192
15 | 125 | 62.5 | 31.25 | 6.25 | 3.6058 | 2.1645 | 2.0833 | 1.25 | 1.2029
25 | 208.3333 | 104.1667 | 52.0833 | 10.4167 | 6.0096 | 3.6075 | 3.4722 | 2.0833 | 2.0048
50 | 416.6667 | 208.3333 | 104.1667 | 20.8333 | 12.0192 | 7.215 | 6.9444 | 4.1667 | 4.0096
75 | 625 | 312.5 | 156.25 | 31.25 | 18.0288 | 10.8225 | 10.4167 | 6.25 | 6.0144
100 | 833.3333 | 416.6667 | 208.3333 | 41.6667 | 24.0385 | 14.43 | 13.8889 | 8.3333 | 8.0192
167 | 1391.6667 | 695.8333 | 347.9167 | 69.5833 | 40.1442 | 24.0981 | 23.1944 | 13.9167 | 13.3921
333 |  |  |  | 138.75 | 80.0481 | 48.0519 | 46.25 | 27.75 | 26.7041
500 |  |  |  | 208.3333 | 120.1923 | 72.1501 | 69.4444 | 41.6667 | 40.0962
833 |  |  |  | 347.0833 | 200.2404 | 120.202 | 115.6944 | 69.4167 | 66.8003
1250 |  |  |  | 520.8333 | 300.4808 | 180.3752 | 173.6111 | 104.1667 | 100.2406
THREE PHASE - LINE CURRENTS
KVA |  |  | RATED LINE VOLTAGE
RATING | 120 | 208 | 240 | 277 | 480 | 4160 | 12000
75 | 360.8439 | 208.1792 | 180.422 | 156.3223 | 90.211 | 10.409 | 3.6084 | VOLTAGE RANGE
100 | 481.1252 | 277.5722 | 240.5626 | 208.4297 | 120.2813 | 13.8786 | 4.8113 | Nominal | Min - Max
150 | 721.6878 | 416.3584 | 360.8439 | 312.6446 | 180.422 | 20.8179 | 7.2169 | 120 | 114 - 126
167 | 803.4791 | 463.5456 | 401.7396 | 348.0776 | 200.8698 | 23.1773 | 8.0348 | 208 | 198 - 218
225 | 1082.5318 | 624.5376 | 541.2659 | 468.9668 | 270.6329 | 31.2269 | 10.8253 | 240 | 228 - 252
300 | 1443.3757 | 832.7167 | 721.6878 | 625.2891 | 360.8439 | 41.6358 | 14.4338 | 277 | 263 - 291
500 | 2405.6261 | 1387.8612 | 1202.8131 | 1042.1485 | 601.4065 | 69.3931 | 24.0563 | 480 | 456 - 504
750 | 3608.4392 | 2081.7918 | 1804.2196 | 1563.2228 | 902.1098 | 104.0896 | 36.0844
1000 | 4811.2522 | 2775.7224 | 2405.6261 | 2084.297 | 1202.8131 | 138.7861 | 48.1125
1500 | 7216.8784 | 4163.5837 | 3608.4392 | 3126.4455 | 1804.2196 | 208.1792 | 72.1688
2000 | 9622.5045 | 5551.4449 | 4811.2522 | 4168.594 | 2405.6261 | 277.5722 | 96.225
2500 | 12028.1306 | 6939.3061 | 6014.0653 | 5210.7425 | 3007.0327 | 346.9653 | 120.2813
3000 | 14433.7567 | 8327.1673 | 7216.8784 | 6252.891 | 3608.4392 | 416.3584 | 144.3376
Print
Main Menu

## OH Data
%Vd =(Vd/Vab)*100 | [5 empty] | ALUMINUM a=0.004200
Vd = IZ |  |  |  | %Vd = (KW/(Vo*cos a))*100*2Z/Vo
KW = VIcos(a) => I = KW/Vcos(a) |  |  |  | T@nC=T@25C(234.5+T@nC)/259.5
Z = Rcos(a) +Xsin(a) |  |  |  | X@D=X@1FOOT(0.528*LOGV@D-0.57)
D>1FOOT
R1/R2=(234.5+T1)/(234.5+T2)
Overhead Conductors
Size /Type | R 25 C | R 75 C | X-RACK | X-XARM | Z-XARM
1/0 AER | 0.1661 | 0.1981 |  | 0.039205 | 0.19538
1/0 BS CU |  | 0.1254 | 0.1034 | 0.11268 | 0.16198
1/0 SSC AL |  | 0.2016 |  | 0.0392 | 0.19853
1/0 THW CU |  | 0.1282 | 0.0684 | 0.077678 | 0.14924
1/0 USA | 0.19508 | 0.21136 | 0.044 |  | 0.20422
1/0 WP AL | 0.168 | 0.20037 | 0.124 | 0.13328 | 0.23843
1/0 WP CU | 0.1022 | 0.12189 | 0.118 | 0.12728 | 0.16518
1000 USA | 0.0223 | 0.024161 | 0.037 |  | 0.03966
2 BS CU |  | 0.1992 | 0.1087 | 0.11798 | 0.23071
2 SSC AL |  | 0.321 |  | 0.0434 | 0.30782
2 SSC CU |  | 0.1957 |  | 0.0434 | 0.19505
2 THW CU |  | 0.1957 | 0.0754 | 0.084678 | 0.21304
2 USA | 0.31061 | 0.33653 | 0.045 |  | 0.31238
2 WP AL | 0.267 | 0.31845 | 0.126 | 0.13528 | 0.34557
2 WP CU | 0.1626 | 0.19393 | 0.118 | 0.12728 | 0.23002
3/0 AER | 0.1046 | 0.12475 |  | 0.036742 | 0.12829
3/0 SSC AL |  | 0.126 |  | 0.0367 | 0.1294
3/0 USA | 0.12197 | 0.13215 | 0.042 |  | 0.13508
3/0 WP AL | 0.134 | 0.15982 | 0.122 | 0.13128 | 0.20106
3336 WP AL | 0.106 | 0.12642 | 0.118 | 0.12728 | 0.16926
336 AER | 0.053 | 0.063212 |  | 0.0348 | 0.07206
350 USA | 0.059848 | 0.064844 | 0.04 |  | 0.076178
4 BS CU |  | 0.3136 | 0.1134 | 0.12268 | 0.33571
4 SSC AL |  | 0.505 |  | 0.0466 | 0.47481
4 SSC CU |  | 0.3092 |  | 0.0466 | 0.29859
4 THW CU |  | 0.3092 | 0.0813 | 0.090578 | 0.31776
4 WP AL | 0.425 | 0.50689 | 0.125 | 0.13428 | 0.51473
4 WP CU | 0.2584 | 0.30819 | 0.118 | 0.12728 | 0.33285
4/0 THW CU |  | 0.0622 | 0.0589 | 0.068178 | 0.085698
4/0 THW CU-UG |  | 0.0653 | 0.041 |  | 0.07708
500 THW CU |  | 0.0276 | 0.0458 | 0.055078 | 0.048848
500 THW CU-UG |  | 0.0289 | 0.039 |  | 0.044755
500 USA | 0.042235 | 0.04576 | 0.039 |  | 0.059255
6 BS CU |  | 0.4993 | 0.1185 | 0.12778 | 0.50507
6 SSC CU |  | 0.4932 |  | 0.0489 | 0.4652
6 THW CU |  | 0.4932 | 0.0867 | 0.095978 | 0.48572
6 WP AL | 0.674 | 0.80387 | 0.128 | 0.13728 | 0.78332
6 WP CU | 0.419 | 0.49973 | 0.118 | 0.12728 | 0.50524

## UG Data
%Vd =(Vd/Vab)*100 | [5 empty] | ALUMINUM a=0.004200
Vd = IZ |  |  |  | %Vd = (KW/(Vo*cos a))*100*2Z/Vo
KW = VIcos(a) => I = KW/Vcos(a) |  |  |  | T@nC=T@25C(234.5+T@nC)/259.5
Z = Rcos(a) +Xsin(a) |  |  |  | X@D=X@1FOOT(0.528*LOGV@D-0.57)
D>1FOOT
R1/R2=(234.5+T1)/(234.5+T2)
Underground Cables
Size /Type | R 65 C | R 90 C | X |  | Z
1/0 AER | 0.1661 | 0.1981 |  | 0.039205 | 0.19538
1/0 BS CU |  | 0.1254 | 0.1034 | 0.11268 | 0.16198
1/0 SSC AL |  | 0.2016 |  | 0.0392 | 0.19853
1/0 THW CU |  | 0.1282 | 0.0684 | 0.077678 | 0.14924
1/0 USA | 0.19508 | 0.21136 | 0.044 |  | 0.20422
1/0 WP AL | 0.168 | 0.20037 | 0.124 | 0.13328 | 0.23843
1/0 WP CU | 0.1022 | 0.12189 | 0.118 | 0.12728 | 0.16518
1000 USA | 0.0223 | 0.024161 | 0.037 |  | 0.03966
2 BS CU |  | 0.1992 | 0.1087 | 0.11798 | 0.23071
2 SSC AL |  | 0.321 |  | 0.0434 | 0.30782
2 SSC CU |  | 0.1957 |  | 0.0434 | 0.19505
2 THW CU |  | 0.1957 | 0.0754 | 0.084678 | 0.21304
2 USA | 0.31061 | 0.33653 | 0.045 |  | 0.31238
2 WP AL | 0.267 | 0.31845 | 0.126 | 0.13528 | 0.34557
2 WP CU | 0.1626 | 0.19393 | 0.118 | 0.12728 | 0.23002
3/0 AER | 0.1046 | 0.12475 |  | 0.036742 | 0.12829
3/0 SSC AL |  | 0.126 |  | 0.0367 | 0.1294
3/0 USA | 0.12197 | 0.13215 | 0.042 |  | 0.13508
3/0 WP AL | 0.134 | 0.15982 | 0.122 | 0.13128 | 0.20106
3336 WP AL | 0.106 | 0.12642 | 0.118 | 0.12728 | 0.16926
336 AER | 0.053 | 0.063212 |  | 0.0348 | 0.07206
350 USA | 0.059848 | 0.064844 | 0.04 |  | 0.076178
4 BS CU |  | 0.3136 | 0.1134 | 0.12268 | 0.33571
4 SSC AL |  | 0.505 |  | 0.0466 | 0.47481
4 SSC CU |  | 0.3092 |  | 0.0466 | 0.29859
4 THW CU |  | 0.3092 | 0.0813 | 0.090578 | 0.31776
4 WP AL | 0.425 | 0.50689 | 0.125 | 0.13428 | 0.51473
4 WP CU | 0.2584 | 0.30819 | 0.118 | 0.12728 | 0.33285
4/0 THW CU |  | 0.0622 | 0.0589 | 0.068178 | 0.085698
4/0 THW CU-UG |  | 0.0653 | 0.041 |  | 0.07708
500 THW CU |  | 0.0276 | 0.0458 | 0.055078 | 0.048848
500 THW CU-UG |  | 0.0289 | 0.039 |  | 0.044755
500 USA | 0.042235 | 0.04576 | 0.039 |  | 0.059255
6 BS CU |  | 0.4993 | 0.1185 | 0.12778 | 0.50507
6 SSC CU |  | 0.4932 |  | 0.0489 | 0.4652
6 THW CU |  | 0.4932 | 0.0867 | 0.095978 | 0.48572
6 WP AL | 0.674 | 0.80387 | 0.128 | 0.13728 | 0.78332
6 WP CU | 0.419 | 0.49973 | 0.118 | 0.12728 | 0.50524

## Menu
SECONDARY VOLTAGE DROP AND FLICKER CALCULATION
Ver 1.2
UG VOLTAGE DROP
OH FLICKER
UG FLICKER
EXIT
CONDUCTOR DATA
MOTOR DATA
PVARR ANALYSIS
OH VOLTAGE DROP

## PVARR
ECONOMIC STUDY - PVARR CALCULATION
CASE:
| 3365 "F" ST SD |  |  | DATE: | 2026-07-29 13:07 | DISCOUNT RATE |  | 10.25 |  | BASE YEAR |  | 1995 |  |  | O&M PVARR
FROM LEVELIZED EOY $
| PREFERRED SOLUTION | Base | FERC | Base Year |  | BK | ESC | PWF | LACC | PWF | % | O&M |  |  | ESC | PWF
|  | Year | Account | Expense |  | LIFE | FCTR | (P/F) |  | (P/A) |  | YEAR | PVARR |  | FCTR | (P/F) | PVARR
1 | STR PRI. ADD XFM, SPLIT SER & SEC. | 1996 | 368.1 | 25000 |  | 34 | 1.029 | 0.90703 | 14.21 | 9.4026 | 0.99 | 247.5 | 33211.0006 |  | 1.063 | 0.8227 | 2035.1601
2 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
3 |  | 0 | 0 | 0 | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total | 0 | 0 | 0
4 |  | 0 | 0 | 0 | PVARR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PVARR | 0 | 0 | 0
5 |  | 0 | 0 | 0 | 33211.0006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33211.0006 | 0 | 0 | 0
NEXT BEST ALTERNATIVE
1 | INSTALL HANDY AUTO AND DEFER XFM FO 6 YEARS | 1996 | 368.1 | 2000 |  | 34 | 1.029 | 0.90703 | 14.21 | 9.4026 | 0.99 | 19.8 | 2656.88 |  | 1.063 | 0.8227 | 162.8128
2 |  | 2002 | 368.1 | 25000 |  | 34 | 1.259 | 0.50507 | 14.21 | 9.4026 | 0.99 | 247.5 | 22629.2334 |  | 1.303 | 0.45811 | 1389.1148
3 |  | 0 | 0 | 0 | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total | 0 | 0 | 0
4 |  | 0 | 0 | 0 | PVARR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PVARR | 0 | 0 | 0
5 |  | 0 | 0 | 0 | 25286.1135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25286.1135 | 0 | 0 | 0
Main Menu
FERC Accounts
Print

## PVARR DOC
PVARR ANALYSIS
CASE:
CUSTOMER ADDRESS / STATION NUMBER |  |  | DATE: | 2026-07-29 13:07
PREFERRED SOLUTION | Base | FERC | Base Year | Total
| Year | Account | Expense | PVARR
Service improvement | 1996 | 368.1 | 25000 | 33211
INSTRUCTIONS
1 - Input customer address or station number for case study.
2 - Input brief description for preferred solution. Examples: Upgrade station, secondary and services,
Replace transformer in kind.
3 - Input the year when improvement / change will be implemented.
4 - Select appropriate FERC account. Click on the FERC macro, copy and paste correct number.
5 - Input total implementation cost. Include all credits for equipment re-furbishing and expenditures.
6 - Repeat steps 2 thru 5 for Next Best Alternative.
7 - When deferring a preferred solution, input implementation of permanent solution on a separate line.
Include the year when it will be implemented, FERC account and total costs.
8 - Select the least cost option.
Print
Main Menu
PVARR

## FERC
ECONOMIC ASSUMPTIONS MANUAL FACTORS
All factors from Interium Economic Assumptions Manual
LACC & Book Life - Table 4-1 Issue Date:08/01/94, O&M - Table 6-1 Issue Date 08/01/94
| DISCOUNT RATE | 10.25
| BASE YEAR | 1995
DISTRIBUTION
FERC | DESCRIPTION | LACC | BK LIFE | O&M
360.1 | LAND | 15.98 | 0 | 0.69
360.2 | LAND RIGHTS | 15.24 | 45 | 0.69
361 | STRUCTURES & IMPROV. | 15.05 | 43 | 2.04
362 | STATION EQUIPMENT | 13.97 | 40 | 5.2
364 | POLES, TOWERS & FIXTURES | 14.71 | 38 | 4.39
365 | OH CONDUCTORS & DEVICES | 14.23 | 41 | 4.39
366 | UG CONDUIT | 14.17 | 41 | 1.17
367 | UG CONDUCTORS & DEVICES | 15.15 | 29 | 1.17
368.1 | LINE TRANSFORMERS | 14.21 | 34 | 0.99
368.2 | PROT. DEV.& CAPACITORS | 18.01 | 16 | 0.99
369.1 | OH SERVICES | 17.27 | 25 | 4.39
369.2 | UG SERVICES | 14.37 | 40 | 1.17
370.1 | METERS | 13.98 | 39 | 6.75
370.2 | METER INSTALLATIONS | 13.82 | 44 | 6.75
371 | INSTL. ON CUST. PREM. | 21.67 | 14 | 0.69
373.2 | STREET LIGHTING | 17.12 | 19 | 3.1
PVAR
Main Menu
Print

## Escalation
Values from Table 3-1 Dated 18 May 1995
ESCLATION FACTORS
| % | % | CUMMULATIVE | COMPOSIT
YEAR | LABOR | PLANT | COMPOSIT *
1994 | 3 | 3 | 0.972 | 1.03
1995 | 0 | 4.4 | 1 | 1.022
1996 | 1.7 | 4 | 1.029 | 1.0285
1997 | 4.9 | 3.8 | 1.063 | 1.0435
1998 | 8.1 | 3.8 | 1.098 | 1.0595
1999 | 3.4 | 3.8 | 1.135 | 1.036
2000 | 3.7 | 3.6 | 1.174 | 1.0365
2001 | 3.7 | 3.5 | 1.216 | 1.036
2002 | 3.7 | 3.5 | 1.259 | 1.036
2003 | 3.8 | 3.7 | 1.303 | 1.0375
2004 | 3.9 | 3.8 | 1.351 | 1.0385
2005 | 4 | 3.9 | 1.402 | 1.0395
2006 | 4 | 3.9 | 1.493 | 1.0395
2007 | 3.9 | 3.9 | 1.552 | 1.039
2008 | 3.9 | 3.8 | 1.611 | 1.0385
2009 | 3.8 | 3.7 | 1.672 | 1.0375
2010 | 3.8 | 3.7 | 1.7347 | 1.0375
2011 | 3.8 | 3.8 | 1.8 | 1.038
2012 | 3.8 | 3.8 | 1.869 | 1.038
2013 | 3.7 | 3.9 | 1.94 | 1.038
2014 | 3.6 | 3.6 | 2.0099 | 1.036
2015 | 3.6 | 3.6 | 2.0822 | 1.036
2016 |  |  | 2.0822
* VALUE CALCULATED BASED ON BASE YEAR, PRE BASE YEAR VALUES ARE ZERO
2009 VALUE USED FOR SUBSEQUENT YEARS