QUESTION 5.1:

- With respect to David Bisi’s testimony on page 7, line 24, to page 8, lines 2-7:

  - Please state the 1-in-10 year cold day demand forecast for core customers on the Southern System that was used in the analysis and identify the year the demand is forecast to occur.

  - Please state the total connected capacity on the Southern System calculated for existing large noncore customers.

  - Did SoCalGas evaluate smaller capacity pipeline projects over the same routes as a part of its analysis?

  - If the answer to the previous question is “yes”:

    - Did the smaller capacity projects keep system pressures above MinOPs and below MAOPs and allow the system linepack to be fully recoverd at the end of the 24 hour simulated period?

    - Please state the pipeline capacity, pipeline diameter and other relevant characteristics, pipeline route and costs associated with each of the smaller capacity projects that were evaluated.

  - If the answer to the previous question is “no”:

    - Please explain in detail why SoCalGas only evaluated an 800 MMcf/d capacity option.

    - Did SoCalGas consider any other pipeline project option other than the three pipeline projects describe in pages 9-14 of Bisi’s testimony?

RESPONSE 5.1:

5.1.1	The 1-in-10 year cold day demand forecast used in the analysis for core customers on the Southern System was 675 million cubic feet per day (MMcfd), where “Southern System” is defined consistent with our responses to SCGC’s 4th Data Request in A.13-12-013, and was originally forecast to occur in 2011.

5.1.2	The total connected capacity on the Southern System for existing large noncore customers (those customers with daily measurement capability) is estimated at 1430 MMcfd.

5.1.3	No.

5.1.4	N/A

5.1.5.1	The purpose of SoCalGas’ and SDG&E’s analyses was to identify the system improvements necessary such that the southern system minimum flowing supply requirement could be eliminated in its entirety.  Multiple “capacity options” were not required to answer that question, and in fact are counter to the design condition presented.

5.1.5.2	Yes.

QUESTION 5.2:

- With respect to David Bisi’s testimony on page 8, lines 8-17:

  - What is the difference between the connected load for noncore customers on the Southern System and the maximum of noncore customer demand on the Southern System during the previous two years?

  - What is the difference between the connected load for noncore customers on the Southern System and the maximum of noncore customer demand on the Southern System forecast to occur during the next five years?

  - Please provide a copy of each forecast of Southern System minimum flows that was used in developing this testimony.

  - Please provide a copy of all forecasts, reports, analyses, memos, notes, or other communications addressing projections of Southern System minimum flows that have been developed or produced by SoCalGas and/or SDG&E during the past five years.

  - What is the total annual volume that SoCalGas projects would flow through the North-South Pipeline in the first full year following its completion?  Please provide the workpapers for this calculation.

  - What is the total annual volume that SoCalGas forecasts would flow through the North-South Pipeline in the fifth full year following its completion?  Please provide the workpapers for this calculation.

  - What is the annual load factor that SoCalGas projects for the North-South Pipeline in the first full year following its completion?  Please provide the workpapers for this calculation.

  - What is the annual load factor that SoCalGas projects for the North-South Pipeline in the fifth full year following its completion?  Please provide the workpapers for this calculation.

RESPONSE 5.2:

5.2.1	SoCalGas does not have readily available the connected load for smaller commercial & industrial noncore customers the Southern System. (where “Southern System is consistent with the definition used in response to SCGC’s 4th Data Request in A.13-12-013), and so cannot provide the difference between the connected load for noncore customers and the maximum estimated demand of noncore customer on the Southern System during the previous two years.  However, the maximum noncore customer estimated demand on the Southern System was 627 MMcfd in 2011, 706 MMcfd in 2012, and 794 MMcfd in 2013.  The noncore demand figures are estimated because a number of smaller commercial & industrial noncore customers on the Southern System have monthly billing cycles and therefore lack recorded daily usage.

5.2.2.	SoCalGas has not developed a forecast of maximum noncore demand on the Southern System.

5.2.3	SoCalGas interprets “Southern System minimum flows” to mean “Southern System minimum flowing supply requirements” for the purposes of this question.  No such forecast was used to develop the testimony cited in this question.

5.2.4	SoCalGas and SDG&E object to this question on the grounds that it requests confidential and proprietary trade secret information.  The request would cover forecasts prepared by Gas Acquisition for its own use, and it could potentially harm SoCalGas/SDG&E and its core customers for such forecasts and forecast methodology to be made public.  The Gas Acquisition forecasts were not used in the preparation of SoCalGas/SDG&E’s testimony in this Application.  Without waiving these objections, and subject thereto, SoCalGas and SDG&E respond as follows:

The attached file was prepared to briefly assess how much North-South capability was needed but was not used in preparation of SoCalGas/SDG&E’s testimony in this Application.

For the purposes of this calculation, the Southern System Minimum flowing supply requirement was calculated as the expected demand on the Southern System minus the estimated backflow capacity including Line 6916.  With the exception of electric generation, seasonal Southern System demand was assumed to remain constant.  Electric generation on the Southern System was estimated using the Energy Portfolio Management Software.  There are times when backflow capability is nearer to zero than to 280,000 dth/d.

5.2.5	SoCalGas has not estimated that figure.

5.2.6	Please refer to the response provided to question 5.2.5.

5.2.7	Please refer to the response provided to question 5.2.5.

5.2.8	Please refer to the response provided to question 5.2.5.

QUESTION 5.3:

- With respect to Beth Musich’s testimony at page 5, Figure 1:

  - Is the figure “Avg. So. Minimum Req.” shown for each year by the blue line equal to the average of the Southern System requirements less the volumes of gas brought from SoCalGas’ Northern System through Chino and Prada and Line 6916?

  - If the answer to the previous question is “no,” please provide a definition of the figures shown by the blue line in Figure 1.

  - Does the red line denoting the volumes of gas delivered by customers demonstrate on average that customer deliveries took care of the Southern System minimum flows during the years shown?

RESPONSE 5.3:

5.3.1	No.

5.3.2	Please refer to SoCalGas Rule No. 41, Utility System Operation, section 5, available on www.socalgas.com.

5.3.3	Figure 1 indicates that while customer deliveries have exceeded the minimum supply requirements for the years shown, deliveries have been decreasing as the minimum supply requirement has been increasing.

QUESTION 5.4:

- With respect to Beth Musich’s testimony at page 16, Figure 3:

  - Do the figures denoted as a red/white striped area correspond to the daily Southern System requirements?

  - If the answer to the previous question is “no,” please explain the relationship between the figures shown by the red/white striped area in Figure 3 and the daily Southern System requirements.

  - Do the figures denoted as a red/white striped area correspond to the daily volumes sent to the Southern System from all sources including gas brought from SoCalGas’ Northern System through Chino and Prada and Line 6916?

  - If the answer to the previous question is “no,” please provide a definition of the figures shown by the red/white striped area in Figure 3.

  - Is the Daily Southern System Minimum (Cycle 4) shown for each day by the blue line equal to the average of the Southern System requirements less the volumes of gas brought from SoCalGas’ Northern System through Chino and Prada and Line 6916?

  - If the answer to the previous question is “no,” please provide a definition of the figures shown by the blue line in Figure 3.

  - Is the CEH Purchases shown for each day by the green line equal to the average of the Southern System requirements less the volumes of gas delivered by customers less the volumes of gas brought from SoCalGas’ Northern System through Chino and Prada and Line 6916?

  - If the answer to the previous question is “no,” please provide a definition of the figures shown by the green line in Figure 3.

  - Why is the blue line virtually equivalent to the top of the red/white striped area on numerous days, that is, what operating conditions cause this occurrence?

RESPONSE 5.4:

5.4.1.	No.

5.4.2.	The height of the red and white area shows total out of state deliveries at the Southern System.  On days when the System Operator made a request for spot purchases, total out of State deliveries at the Southern System were close or equal to the Southern System minimum.  For further explanation, please refer to Response 5.4.9.

5.4.3.	No.

5.4.4.	The height of the red and white area displays the sum of all deliveries at El Paso – Ehrenberg, NBP – Blythe, and TGN – Otay Mesa on Cycle 5.  These volumes include purchases by the California Energy Hub (CEH).

5.4.5.	No.

5.4.6.	The blue line shows the Southern System Minimum Flowing Supply Requirement posted on Envoy.  For an explanation on how this is calculated, please refer to Response 5.3.2.

5.4.7.	No.

5.4.8.	The height of the green area displays the deliveries made by the CEH at El Paso – Ehrenberg and NBP – Blythe in response to a request by the System Operator.

5.4.9.	When scheduled deliveries at the Southern System fell below the Southern System Minimum, the CEH, on behalf of the system operator, purchased and delivered volumes close or equal to the shortfall.  On such days, the spot purchases made by the CEH increased total deliveries into the Southern System to levels close or equal to the Southern System Minimum Flowing Supply Requirement.