## Dialog1 (hidden)
Volt Drop and Flicker 2000
120/240
120/208
240/480
277/480
Single Phase Residential
Single Phase Array
Three Phase Commercial.
OverHead
Update
OK
1 PH
3 PH
General Information
Phase
Voltage
Power Factor
Work Order Number
DPSS#
Title
Designer
UG Service OH Source
Single Phase OverHead

## Open
Voltdrop & Flicker 2000
|  | Phase | 1
Title
|  | Lookup | 2 | Planner
| 4 | 1 | Single ph
|  | 2 | Array | Dpss #
|  | 3 | Three ph |  |  | 0.9
| 1 | Voltage | 1 | Power Fact | 0.9 | 0.85
| 2 |  |  |  |  | 0.85
| 4 |  |  | WO
Version 5A
Basic Info

## Single PH
Single Phase Underground Voltage Drop and Flicker
| Title |  | 0 |  |  | Total Demand |  | Power Factor
[6 empty] | KW |  | 0.9 | %
| Designer |  | 0 |  |  | Transformer |  | 0 | % V.D.
[7 empty] | KVA |  | Loading
| DPSS # |  | 0 |  |  | 15 | KVA |  | 0%
Transformer Size
| Work Order # |  |  | 0
|  | Footage | [6 empty] | Footage
|  | Demand | [6 empty] | Demand
|  | % Volt Drop | [6 empty] | % Volt Drop
|  | % Flicker | [6 empty] | % Flicker
|  | Ampacity | [6 empty] | Ampacity
| Cable |  | Motor Size |  |  |  |  | Cable |  | Motor Size
Secondary
Footage
[10 empty] | Cable |  | Demand
% Volt Drop
% Flicker
Ampacity
Transformer or Lot #
| Voltage | 120 | 240 | Phase | 1
Version 5A
Print
Reset
Basic Info

## SINGLE PH ARRAY
Single Phase Underground Voltage Drop and Flicker Array
|  | Title |  | 0 |  |  |  | Total Demand |  |  | Power Factor |  | Number of Houses |  |  |  | Base KW |  |  | Motor Load
[8 empty] | KW |  |  | 0.9 | % | STA |  | Total #
|  | Designer |  | 0 |  |  |  | Transformer |  |  | 0 | % V.D. | 1 |  | Total # |  | Transformer and
[9 empty] | KVA |  |  | Loading | 2 |  | Total # |  | Secondary |  |  | Diversity Factor
|  | DPSS # |  | 0 |  |  |  | 15 | KVA |  |  | 0% | 3 |  | Total # |  | Load
[8 empty] | Transformer Size |  |  |  |  | 4 |  | Total #
|  | Work Order # |  |  | 0
|  |  | Footage |  |  |  | Footage |  |  |  | Footage |  |  |  |  | Footage |  |  |  | Footage
|  |  | Demand |  |  |  | Demand |  |  |  | Demand |  |  |  |  | Demand |  |  |  | Demand |  | #N/A | Trans
|  |  | % Volt Drop |  |  |  | % Volt Drop |  |  |  | % Volt Drop |  |  |  |  | % Volt Drop |  |  |  | % Volt Drop |  | #N/A | Ser 1
|  |  | % Flicker |  |  |  | % Flicker |  |  |  | % Flicker |  |  |  |  | % Flicker |  |  |  | % Flicker |  | #N/A | Ser 2
|  |  | Ampacity |  |  |  | Ampacity |  |  |  | Ampacity |  |  |  |  | Ampacity |  |  |  | Ampacity |  | #N/A | Ser 3
|  | Cable |  | Motor Load |  | Cable |  | Motor Load |  | Motor Load |  | Cable |  |  | Motor Load |  | Cable |  | Motor Load |  | Cable | #N/A | Ser 4
Transformer / lot number
[5 empty] | Cable |  |  |  |  | Cable |  | 1 |  |  | Cable |  |  |  | Cable
|  |  |  | Secondary 4 |  |  |  |  | Secondary 2 |  |  |  |  | Secondary 1 |  |  |  | Secondary 3
[5 empty] | Footage |  |  |  |  | Footage |  |  |  |  | Footage |  |  |  | Footage
[5 empty] | Demand |  |  |  |  | Demand |  |  |  |  | Demand |  |  |  | Demand
[5 empty] | % Volt Drop |  |  |  |  | % Volt Drop |  |  |  |  | % Volt Drop |  |  |  | % Volt Drop
[5 empty] | Ampacity |  |  |  |  | Ampacity |  |  |  |  | Ampacity |  |  |  | Ampacity
|  |  | Footage |  |  |  | Footage |  |  |  | Footage |  |  |  |  | Footage |  |  |  | Footage
|  |  | Demand |  |  |  | Demand |  |  |  | Demand |  |  |  |  | Demand |  |  |  | Demand
|  |  | % Volt Drop |  |  |  | % Volt Drop |  |  |  | % Volt Drop |  |  |  |  | % Volt Drop |  |  |  | % Volt Drop
|  |  | % Flicker |  |  |  | % Flicker |  |  |  | % Flicker |  |  |  |  | % Flicker |  |  |  | % Flicker
|  |  | Ampacity |  |  |  | Ampacity |  |  |  | Ampacity |  |  |  |  | Ampacity |  |  |  | Ampacity
|  | Cable |  | Motor Load |  | Cable |  | Motor Load |  | Motor Load |  | Cable |  |  | Motor Load |  | Cable |  | Motor Load |  | Cable
|  |  | Voltage | 120 | 240 | Phase | 1
Version 5A
Fill Ref
| 1 | 1 | 1 | 5 | 5
1 | 5 | 5 | 5 | 5 | 5
3
2
3
Basic Info
Fill
Fill
Reset
Print
Fill

## THREE PH
Three Phase Underground Voltage Drop and Flicker
Per Design Manual 3Ph Power Factor to be .85
Select Basic Info to change Factor.
Title |  | 0 |  |  |  |  | Total Demand |  |  |  | Power Factor
[7 empty] | KW | 0 |  | 0.9
Designer |  | 0 |  |  |  |  | Transformer |  |  |  | % V.D.
[8 empty] | KVA |  | Loading
DPSS # |  | 0 |  |  |  |  | 75 | KVA |  |  | N/A
[7 empty] | Transformer Size |  |  |  | Taps
Work Order # |  |  | 0 | [5 empty] | Select a larger
Transformer
Ampacity |  | Footage | 81 |  |  | Ampacity |  | Footage |  |  |  | Ampacity |  | Footage
|  | Demand | 52 |  |  |  |  | Demand | [5 empty] | Demand
Cable |  | % Volt Drop |  |  |  | Cable |  | % Volt Drop |  |  |  | Cable |  | % Volt Drop
|  | % Flicker | [5 empty] | % Flicker | [5 empty] | % Flicker
Runs |  |  | Motor H.P. |  |  | Runs |  |  | Motor H.P. |  |  | Runs |  |  | Motor H.P.
[13 empty] | Runs |  | Cable
Footage
[12 empty] | #N/A |  | Demand
[12 empty] | #DIV/0! |  | % Volt Drop
[12 empty] | #N/A |  | % Flicker
Transformer or Lot # | [13 empty] | Ampacity
| Voltage | 120 | 240 | Phase | 1
Version 5A
0
Reset
Print
Basic Info

## OverHeadUG
Single Phase Underground Voltage Drop and Flicker W/ OH Source
| Title |  | 0 |  |  |  | Total Demand |  | Power Factor
[7 empty] | KW |  | 0.9 | %
| Designer |  | 0 |  |  |  | Transformer |  | 0% | V.D.
[8 empty] | KVA |  | Loading
| DPSS # |  | 0 |  |  |  | 15 | KVA |  | 0%
Transformer Size
| Work Order # |  |  | 0
Footage
|  |  |  | Footage | [5 empty] | Demand
|  |  |  | Demand | [5 empty] | % Volt Drop
|  |  |  | % Volt Drop | [5 empty] | % Flicker
|  |  |  | % Flicker | [5 empty] | Ampacity
|  |  |  | Ampacity |  |  |  |  | Cable
|  |  |  | Cable |  | Motor Size
Footage
Demand
% Volt Drop
|  | Footage |  |  |  | % Flicker
|  | Demand |  |  |  | Ampacity |  |  |  | Footage
|  | % Volt Drop |  |  | Cable |  |  |  |  | Demand
|  | % Flicker | [7 empty] | % Volt Drop
|  | Ampacity | [7 empty] | % Flicker
Cable |  |  | Motor Size | [6 empty] | Ampacity
[9 empty] | Cable |  | Motor Size
Version 5A
| Voltage | 120 | 240 | Phase | 1
Print
Reset
Basic Info

## OverHead
Single Phase OverHead Voltage Drop and Flicker
Title |  | 0 |  |  |  | Total Demand |  |  | Power Factor
[6 empty] | KW |  |  | 0.9 | %
Designer |  | 0 |  |  |  | Transformer |  |  | 0% | V.D.
[7 empty] | KVA |  |  | Loading
DPSS # |  | 0 |  |  |  | 15 | KVA |  |  | 0%
Transformer Size
Work Order # |  |  | 0
Footage
|  |  | Footage | [6 empty] | Demand
|  |  | Demand | [6 empty] | % Volt Drop
|  |  | % Volt Drop | [6 empty] | % Flicker
|  |  | % Flicker | [6 empty] | Ampacity
|  |  | Ampacity | [7 empty] | Cable
|  |  | Cable |  | Motor Size
| Footage | [7 empty] | Footage
| Demand | [7 empty] | Demand
| % Volt Drop | [7 empty] | % Volt Drop
| % Flicker | [7 empty] | % Flicker
| Ampacity | [7 empty] | Ampacity
Cable |  |  | Motor Size |  |  |  |  | Cable |  |  | Motor Size
Version 5A
Voltage | 120 | 240 | Phase | 1
Print
Reset
Basic Info

## UGVDROP1 (hidden)
[9 empty] | Wire Ref 3PH | 2 | [6 empty] | Ampicity | Check
| Footage | Ser Kw | Transformer | Trans Kw |  |  |  |  | Volt Drop 3ph | 0 |  | CONDUCTOR DATA DESIGN MANUAL |  |  |  |  | 1 PH | OK
Single PH | 0 | 0 | 15 | 0 |  |  |  |  | Wire Ref 1PH | 1 | ALUMINUM CABLES OHMS / 1000 FT |  |  |  | Volt Drop | Amp Check | 3 PH | OK
Array | 0 | 0 | 15 | 0 |  |  |  |  | Volt Drop | 0 | SIZE | R | X | Z |  | 1 through 7 | 7 through 12
Three PH | 81 | 52 | 75 | 0 | [5 empty] | 1 | 2 | 0.267 | 0.0238 | 0.25067 | 0 | OK | NO
UgSerOh | 0 | 0 | [7 empty] | 2 | 1/0 | 0.168 | 0.0241 | 0.1617 | 0 | OK | NO
[9 empty] | 1 | 3 | 3/0 | 0.105 | 0.0226 | 0.10435 | 0 | OK | NO
[9 empty] | 2 | 4 | 350 | 0.0505 | 0.0215 | 0.054822 | 0 | OK | NO
PF | ANGLE |  | 1-PH = 1 | SYSTEM |  | Cable Demand | KW |  | 3 | 5 | 500 | 0.0354 | 0.0207 | 0.040883 | 0 | OK | NO
0.9 | 25.8419 |  | 3-PH = 3 | 1 |  |  | 0 |  | 4 | 6 | 1000 | 0.0177 | 0.0199 | 0.024604 | 0 | OK | NO
VOLTAGE |  |  | RUN |  | FEET |  | L-AMPS |  |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C
120 | 240 |  | 1 |  | 0 |  | 0 |  |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | 600 Volt Secondary Aluminum Cable, DB Conduit (Direct Buried)
|  |  | IF 3 PH | [7 empty] | SIZE | R@65C | R@90C | X | Z | R@90C | Z |  | (With 7-1/2 Inches Centerline to Centerline Spacing Between Conduits)
|  |  | 1 | [7 empty] | 2 | 0.31061 | 0.33653 | 0.045 | 0.32249 | 0.2052 | 0.2043 |  | Cable Size | Conduit | Number of | Number of Runs
[11 empty] | 1 | 0.24432 | 0.26471 | 0.046 | 0.25829 | 0.1623 | 0.16612 |  | Size | Size | Conductors | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Single-Phase Transformers |  |  |  | Three-Phase Transformers | [6 empty] | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.2094 | 0.1334 | 0.13924 |  | 1000 | 5"DB | 3-1/C | 605 | 1104 | 1527 | 1892 | 2335 | 2526 | 2821 | 3080 | 3339 | 3550 | 3707 | 3828
[11 empty] | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.16944 | 0.1028 | 0.11126 |  | 500 | 4"DB | 3-1/C | 397 | 736 | 1029 | 1288 | 1595 | 1746 | 1953 | 2144 | 2313 | 2470 | 2607 | 2712
kVA |  | 15 |  | kVA |  | 75 |  |  |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.13724 | 0.0825 | 0.092557 |  | 350 | 3"DB | 2-1/C | 318 | 600 | 852 | 1076 | 1285 | 1482 | 1673 | 1840 | 2016 | 2160 | 2266 | 2376
Percentage Load |  | 0% |  | Percentage Load |  | N/A |  |  |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.11354 | 0.0653 | 0.076641 |  | 350 | 3"DB | 3-1/C | 313 | 586 | 822 | 1036 | 1230 | 1416 | 1589 | 1760 | 1908 | 2040 | 2145 | 2232
%Transformer Volt Drop |  | 0 |  | %Transformer Volt Drop |  | 0 |  |  |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.098578 | 0.0552 | 0.067551 |  | 3/0 | 2"DB | 2-1/C | 202 | 386 | 552 | 704 | 875 | 984 | 1113 | 1232 | 1250 | 1440 | 1518 | 1608
Load on Transformer |  | 0 | KW |  |  | 0 | KW |  |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075795 | 0.0404 | 0.053796 |  | 3/0 | 3"DB | 3-1/C | 199 | 376 | 534 | 676 | 810 | 936 | 1057 | 1160 | 1269 | 1350 | 1419 | 1500
[11 empty] | 500 | 0.042235 | 0.04576 | 0.039 | 0.058184 | 0.0289 | 0.04301 |  | 1/0 | 2"DB | 2-1/C | 152 | 292 | 420 | 536 | 645 | 750 | 854 | 944 | 1044 | 1130 | 1188 | 1248
[11 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.043965 | 0.0199 | 0.034474 |  | #2 | 2"DB | 2-1/C | 113 | 218 | 315 | 404 | 490 | 570 | 651 | 720 | 792 | 860 | 913 | 960
[11 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.037873 | 0.0157 | 0.030258 |  | #8 | 1"DB | 1/C | 47 | 92 | 135 | 176 | 215 | 252 | 287 | 320 | 306 | 380 | 407 | 432
Ampacity OK |  | ALUMINUM CABLES |  |  |  | COPPER CABLES
Yes or No | Yes or No |  |  |  | TRANS. + CABLE |  |  | TRANS. + CABLE |  |  |  | 0.023 | 0.024115 |  | 0.077 | 0.080732
1-7 Runs | 8-12 Runs | SIZE | V - DROP | % DROP | %V-DROP | V - DROP | % DROP | V-DROP
OK | NO | 2 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Single Phase Padmount Transformer Size
|  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | kVA
OK | NO | 1/0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Percentage | 15 | 25 | Number of Runs 1: 50; Number of Runs 2: 75; Number of Runs 3: 100; Number of Runs 4: 167; Number of Runs 5: Under 50% Loading; Number of Runs 8: Select a larger Transformer
|  | 2/0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 50% | 1 | 1 | Number of Runs 1: 1; Number of Runs 2: 0.9; Number of Runs 3: 0.9; Number of Runs 4: 1; Number of Runs 6: 0; Number of Runs 8: Transformer
OK | NO | 3/0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 60% | 1.2 | 1.2 | Number of Runs 1: 1.2; Number of Runs 2: 1.1; Number of Runs 3: 1; Number of Runs 4: 1.2; Number of Runs 5: Over 50% Loading
|  | 4/0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 70% | 1.5 | 1.4 | Number of Runs 1: 1.4; Number of Runs 2: 1.3; Number of Runs 3: 1.2; Number of Runs 4: 1.4; Number of Runs 6: #N/A
|  | 250 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 50 |  | 80% | 1.7 | 1.6 | Number of Runs 1: 1.6; Number of Runs 2: 1.5; Number of Runs 3: 1.4; Number of Runs 4: 1.6
OK | NO | 350 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 90% | 1.9 | 1.8 | Number of Runs 1: 1.8; Number of Runs 2: 1.6; Number of Runs 3: 1.6; Number of Runs 4: 1.8
OK | NO | 500 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | #VALUE! |  | 100% | 2.1 | 2 | Number of Runs 1: 1.8; Number of Runs 2: 1.8; Number of Runs 3: 1.7; Number of Runs 4: 2
|  | 750 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 60% |  | 110% | 2.3 | 2.2 | Number of Runs 1: 2; Number of Runs 2: 2; Number of Runs 3: 1.9; Number of Runs 4: 2.2
OK | NO | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 |  | 120% | 2.5 | 2.4 | Number of Runs 1: 2.2; Number of Runs 2: 2.2; Number of Runs 3: 2.1; Number of Runs 4: 2.4
[17 empty] | 0 |  | 130% | 2.7 | 2.6 | Number of Runs 1: 2.4; Number of Runs 2: 2.4; Number of Runs 3: 2.3; Number of Runs 4: 2.6
[19 empty] | 140% | 2.9 | 2.8 | Number of Runs 1: 2.6; Number of Runs 2: 2.5; Number of Runs 3: 2.4; Number of Runs 4: 2.9
[7 empty] | 3 | [9 empty] | 1.35 |  | 150% | 3.1 | 3 | Number of Runs 1: 2.8; Number of Runs 2: 2.7; Number of Runs 3: 2.6; Number of Runs 4: 3.1
[17 empty] | 1 |  | 160% | 3.3 | 3.2 | Number of Runs 1: 2.9; Number of Runs 2: 2.9; Number of Runs 3: 2.8; Number of Runs 4: 3.3
Number of Runs |  | Diversity factors |  | Ref Cell | 3 | [11 empty] | 50kVA |  | 170% | 3.5 | 3.4 | Number of Runs 1: 3; Number of Runs 2: 3.1; Number of Runs 3: 3.3; Number of Runs 4: 3.6
1 |  |  |  |  | Base Load | [11 empty] | 70%
2 |  | LOAD | 0 | kw | S F Detached W/AC | [11 empty] | #N/A |  | 120/208V Three-Phase Padmount Transformer Size
3 |  |  |  |  | S.M. M F Attached W/AC | [13 empty] | Transformer | Kva
4 |  | STA | 0 | #N/A | #N/A | #N/A | [12 empty] | Loading | 45 | 75 | Number of Runs 1: 150; Number of Runs 2: 225; Number of Runs 3: 300; Number of Runs 4: 500; Number of Runs 5: 750; Number of Runs 6: 1000
5 |  | 1 | 0 | #N/A | #N/A | #N/A | [12 empty] | 50% | 1.3 | 1.13 | Number of Runs 1: 0.89; Number of Runs 2: 0.91; Number of Runs 3: 0.98; Number of Runs 4: 1.54; Number of Runs 5: 2.03; Number of Runs 6: 1.9
6 |  | 2 | 0 | #N/A | #N/A | #N/A | [12 empty] | 60% | 1.6 | 1.35 | Number of Runs 1: 1.07; Number of Runs 2: 1.1; Number of Runs 3: 1.17; Number of Runs 4: 1.8; Number of Runs 5: 2.43; Number of Runs 6: 2.33
7 |  | 3 | 0 | #N/A | #N/A | #N/A | [12 empty] | 70% | 1.8 | 1.58 | Number of Runs 1: 1.2; Number of Runs 2: 1.3; Number of Runs 3: 1.37; Number of Runs 4: 2.1; Number of Runs 5: 2.84; Number of Runs 6: 2.72
8 |  | 4 | 0 | #N/A | #N/A | #N/A | [12 empty] | 80% | 2.1 | 1.81 | Number of Runs 1: 1.43; Number of Runs 2: 1.46; Number of Runs 3: 1.56; Number of Runs 4: 2.4; Number of Runs 5: 3.2; Number of Runs 6: 3
9 | [18 empty] | 90% | 2.4 | 2.03 | Number of Runs 1: 1.6; Number of Runs 2: 1.64; Number of Runs 3: 1.76; Number of Runs 4: 2.7; Number of Runs 5: 3.6; Number of Runs 6: 3.4
10 | [18 empty] | 100% | 2.6 | 2.26 | Number of Runs 1: 1.78; Number of Runs 2: 1.83; Number of Runs 3: 1.9; Number of Runs 4: 3; Number of Runs 5: 4; Number of Runs 6: 3.8
11 |  |  |  | Base Load | S F Atached W/AC |  | M F Atached W/AC | [11 empty] | 110% | 2.9 | 2.48 | Number of Runs 1: 1.96; Number of Runs 2: 2.01; Number of Runs 3: 2.1; Number of Runs 4: 3.3; Number of Runs 5: 4.3; Number of Runs 6: 4.2
12 |  |  |  | 1 | 2 | 3 | [12 empty] | 120% | 3.2 | 2.71 | Number of Runs 1: 2.14; Number of Runs 2: 2.2; Number of Runs 3: 2.3; Number of Runs 4: 3.6; Number of Runs 5: 4.7; Number of Runs 6: 4.6
|  | 1 | A | 1 | 1 | 1 | [12 empty] | 130% | 3.4 | 2.94 | Number of Runs 1: 2.39; Number of Runs 2: 2.49; Number of Runs 3: 2.72; Number of Runs 4: 4; Number of Runs 5: 5.4; Number of Runs 6: 5.2
|  | 2 | B | 1 | 1 | 1 | [12 empty] | 140% | 3.7 | 3.16 | Number of Runs 1: 2.57; Number of Runs 2: 2.68; Number of Runs 3: 2.93; Number of Runs 4: 4.44; Number of Runs 5: 5.9; Number of Runs 6: 5.6
|  | 3 | C | 0.75 | 0.85 | 0.7 | [12 empty] | 150% | 4 | 3.69 | Number of Runs 1: 2.91; Number of Runs 2: 3.07; Number of Runs 3: 3.37; Number of Runs 4: 5; Number of Runs 5: 6.8; Number of Runs 6: 6.5
|  | 4 | D | 0.75 | 0.85 | 0.7
|  | 5 | E | 0.65 | 0.8 | 0.65
|  | 6 | F | 0.65 | 0.8 | 0.65 | [12 empty] | 277/480V Three-Phase Padmount Transformer Size
|  | 7 | G | 0.65 | 0.8 | 0.65 | [12 empty] | Transformer | Kva
|  | 8 | H | 0.55 | 0.75 | 0.65 | [12 empty] | Loading | 75 | 150 | 225 | 300 | 500 | 750 | 1000 | 1500 | 2000 | 2500 | 3000
|  | 9 | I | 0.55 | 0.75 | 0.65 | [12 empty] | 50% | 1.07 | 0.92 | 0.72 | 0.96 | 0.93 | 1.93 | 1.9 | 1.9 | 1.8 | 1.8 | 1.9
|  | 10 | J | 0.55 | 0.75 | 0.65 | [12 empty] | 60% | 1.29 | 1.1 | 0.87 | 1.15 | 1.12 | 2.32 | 2.34 | 2.34 | 2.2 | 2.2 | 2.2
|  | 11 | K | 0.55 | 0.75 | 0.65 | [12 empty] | 70% | 1.5 | 1.3 | 1.01 | 1.3 | 1.3 | 2.6 | 2.73 | 2.6 | 2.63 | 2.6 | 2.6
|  | 12 | L | 0.55 | 0.75 | 0.65 | [12 empty] | 80% | 1.72 | 1.47 | 1.16 | 1.54 | 1.49 | 3 | 3 | 3 | 2.9 | 3.04 | 3
|  | 13 | M | 0.55 | 0.75 | 0.65 | [12 empty] | 90% | 1.93 | 1.65 | 1.3 | 1.73 | 1.68 | 3.4 | 3.4 | 3.4 | 3.3 | 3.3 | 3.3
|  | 14 | N | 0.55 | 0.75 | 0.65 | [12 empty] | 100% | 2.1 | 1.84 | 1.4 | 1.92 | 1.86 | 3.8 | 3.8 | 3.8 | 3.7 | 3.7 | 3.7
|  | 15 | O | 0.5 | 0.7 | 0.6 | [12 empty] | 110% | 2.36 | 2.02 | 1.59 | 2.11 | 2 | 4.1 | 4.2 | 4.2 | 4 | 4.1 | 4.1
Transformer | Single Ph |  | Volt Drop at 100 % Loading |  | Voltage lookup | Ph Ref Cell | 1 | [11 empty] | 120% | 2.58 | 2.21 | 1.73 | 2.31 | 2.24 | 4.5 | 4.6 | 4.5 | 4.4 | 4.4 | 4.4
Ref Cell | 1 | [17 empty] | 130% | 2.79 | 2.5 | 1.88 | 2.6 | 2.5 | 5.2 | 5.2 | 5.3 | 5.1 | 5.2 | 5.2
1 | 15 KVA | 15 | 2.1 |  | 1 | 120 | 240 | [11 empty] | 140% | 3.01 | 2.6 | 2.1 | 2.8 | 2.7 | 5.6 | 5.6 | 5.7 | 5.5 | 5.6 | 5.7
2 | 25 KVA | 25 | 2 |  | 2 | 120 | 208 | [11 empty] | 150% | 3.5 | 3 | 2.4 | 3.3 | 3.1 | 6.4 | 6.5 | 6.5 | 6.3 | 6.4 | 6.5
3 | 50 KVA | 50 | 1.8 |  | 3 | 240 | 480
4 | 75 KVA | 75 | 1.8 |  | 4 | 277 | 480
5 | 100 KVA | 100 | 1.7 |  | Voltage Ref | 1
6 | 167 KVA | 167 | 2
2

## UGFLCKER1 (hidden)
[36 empty] | 15 | 2.1 | 1.7 | 1.2 | updated 17th Feb. 2000 with table 5 of 5413.7
[36 empty] | 25 | 2 | 1.6 | 1.2
[36 empty] | 50 | 2.1 | 1.3 | 1.7
[36 empty] | 75 | 2 | 1.1 | 1.8 | 1.051 | 1.751
[36 empty] | 100 | 2.2 | 1.1 | 1.9
[19 empty] | LRC VALUES (updated 5 FEB 1998) | [15 empty] | Single Phase kVA | 167 | 2.3 | 1.1 | 2
[20 empty] | SINGLE-PHASE MOTOR SIZES IN HP | [15 empty] | 45 | 2.7153 | 1.91 | 1.93
[19 empty] | VOLTAGE | 1 | 1.5 | 2 | [13 empty] | 75 | 2.2888 | 1.72 | 1.51 | 1.62 | 1.46
[19 empty] | 120 | 46 | 69 | 92 | [13 empty] | 150 | 1.916 | 1.14 | 1.54
[36 empty] | 225 | 1.9462 | 1.19 | 1.54
[13 empty] | CONDUCTOR DATA DESIGN MANUAL | [22 empty] | 300 | 2.2897 | 1.02 | 2.05
PF |  | ANGLE |  | 1-PH = 1 |  | # OF PHASES | HP | 1Ph-LRC | 1Ph-XKMR% | R |  | ALUMINUM CABLES OHMS / 1000 FT | [23 empty] | 500 | 4.5034 | 0.81 | 4.43
0.75 |  | 41.4096 |  | 3-PH = 3 |  | 1 | 1 | 27 | 0.89369 | 1.7 | 1-Ph | SIZE | R | X | Z | L-AMPS |  |  | LRC VALUES (updated 5 FEB 1998) | [16 empty] | 750 | 6.0451 | 0.95 | 5.97
[8 empty] | 3Ph-LRC |  | #N/A | 3-Ph | 2 | 0.267 | 0.0238 | 0.21599 | 27 |  |  |  | SINGLE-PHASE MOTOR SIZES IN HORSE POWER | [15 empty] | 1000 | 5.82 | 0.9 | 5.75
[8 empty] | n/a |  | X |  | 1/0 | 0.168 | 0.0241 | 0.14194 |  |  |  | VOLTAGE | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 10 | [7 empty] | 1500 | 0 | 0 | 0
VOLTAGE |  |  |  | RUN |  | FEET | KW | XFMR KVA | 3Ph-XFMR % | 1.2 | 1-Ph | 3/0 | 0.105 | 0.0226 | 0.093698 |  |  |  | 240 | 27 | 34 | 46 | 69 | 103 | 115 | 140 | 175 | 218 | [7 empty] | 2000 | 0 | 0 | 0
120 |  | 240 |  | 1 |  | 0 | 4.86 | 15 | 0 | #N/A |  | 350 | 0.0505 | 0.0215 | 0.052096 | [20 empty] | 2500 | 0 | 0 | 0
[12 empty] | 500 | 0.0354 | 0.0207 | 0.040242 | [20 empty] | 3000 | 0 | 0 | 0
ALUMINUM CABLES | [6 empty] | COPPER CABLES | [27 empty] | Three Phase kVA | Three Phase kVA | Z% | R% | X%
|  | CABLE |  | CABLE |  | *TOTAL% | CABLE | CABLE | *TOTAL% |  |  | 1000 | 0.0177 | 0.0199 | 0.026438 | [20 empty] | updated 17th Feb. 2000 with table 9 of 5413.7
SIZE |  | (VOLTS) |  | ( % ) |  | FLICKER | (VOLTS) | ( % ) | FLICKER |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C | [6 empty] | LRC VALUES (updated 31dec1997)
2 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | MOTOR SIZES IN HORSE POWER
1 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | SIZE | R@65C | R@90C | X | Z | R@90C | Z | VOLTAGE | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200
1/0 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 2 | 0.31061 | 0.33653 | 0.045 | 0.28216 | 0.2052 | 0.18366 | 208 | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
2/0 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 1 | 0.24432 | 0.26471 | 0.046 | 0.22896 | 0.1623 | 0.15215 | 240 | 64 | 85 | 92 | 106 | 127 | 162 | 232 | 290 | 365 | 435 | 580 | 725 | 1085 | 1450 | 2170
3/0 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.18762 | 0.1334 | 0.12915 | 480 | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
4/0 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.15403 | 0.1028 | 0.10554
250 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.12689 | 0.0825 | 0.089655
350 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.10684 | 0.0653 | 0.076094
500 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.094374 | 0.0552 | 0.068519
750 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075091 | 0.0404 | 0.056758 |  | 3 Phase | Three-Phase Motor (Sized in HP) | [15 empty] | Transformer Data |  | X/R
1000 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 500 | 0.042235 | 0.04576 | 0.039 | 0.060116 | 0.0289 | 0.047471 |  | Trans | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200 | R | X | Ratio | Z%
[12 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.047969 | 0.0199 | 0.04006 |  | 45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.0191 | 0.0193 | 1.0105 | 2.715%
[12 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.042594 | 0.0157 | 0.036248 |  | 75 | 0.66522 | 0.88072 | 0.95567 | 1.0962 | 1.3117 | 1.6771 | 2.4079 | 3.0076 | 3.7852 | 4.5066 | 6.0057 | 7.5142 | 11.2432 | 15.019 | 22.4864 | 30.0474 | 0.0172 | 0.0151 | 0.87791 | 2.289%
WITH REDUCED LRC TO 770A OR 50HP | [6 empty] | *TOTAL FLICKER = CABLE (%) + XMFR (%) | [12 empty] | 150 | 0.3078 | 0.40751 | 0.44219 | 0.54094 | 0.60693 | 0.776 | 1.1141 | 1.3916 | 1.7514 | 2.0852 | 2.7789 | 3.4768 | 5.2022 | 6.9493 | 10.4045 | 13.903 | 0.0114 | 0.0154 | 1.3509 | 1.916% |  | 1.62% | 1.46% | 0.90123 | 2.181%
[13 empty] | 0.023 | 0.024115 |  | 0.077 | 0.080732 |  |  | 225 | 0.20691 | 0.27393 | 0.29724 | 0.34096 | 0.40798 | 0.52163 | 0.74894 | 0.93544 | 1.1773 | 1.4017 | 1.868 | 2.3372 | 3.497 | 4.6714 | 6.994 | 9.3457 | 0.0119 | 0.0154 | 1.2941 | 1.946% |  | 1.25% | 1.47% | 1.176 | 1.93%
[20 empty] | 300 | 0.19214 | 0.25438 | 0.27603 | 0.31663 | 0.37887 | 0.48441 | 0.69549 | 0.86869 | 1.0933 | 1.3017 | 1.7347 | 2.1704 | 3.2474 | 4.338 | 6.4949 | 8.6788 | 0.0102 | 0.0205 | 2.0098 | 2.29% |  | 0.88% | 1.32% | 1.5 | 1.586%
Lookup Value |  |  | 1ph | 0 | 3ph | 0 | [13 empty] | 500 | 0.22773 | 0.3015 | 0.32716 | 0.37527 | 0.44904 | 0.57413 | 0.82432 | 1.0296 | 1.2958 | 1.5428 | 2.056 | 2.5724 | 3.8489 | 5.1415 | 7.6979 | 10.2863 | 0.0081 | 0.0443 | 5.4691 | 4.503% |  | 1.16% | 1.77% | 1.5259 | 2.116%
Lookup |  | Wire |  | Volatge Drop |  | % Volatge Drop | [13 empty] | 750 | 0.20315 | 0.26896 | 0.29185 | 0.33476 | 0.40057 | 0.51216 | 0.73534 | 0.91846 | 1.1559 | 1.3763 | 1.8341 | 2.2947 | 3.4335 | 4.5866 | 6.867 | 9.176 | 0.0095 | 0.0597 | 6.2842 | 6.045% |  | 0.9% | 2.07% | 2.3 | 2.257%
1 |  | 2 |  | 0 |  | 0 | [13 empty] | 1000 | 0.14663 | 0.19413 | 0.21065 | 0.24163 | 0.28913 | 0.36968 | 0.53076 | 0.66294 | 0.83435 | 0.99337 | 1.3238 | 1.6563 | 2.4783 | 3.3106 | 4.9565 | 6.6232 | 0.009 | 0.0575 | 6.3889 | 5.82% |  | 0.82% | 5.81% | 7.0854 | 5.868%
2 |  | 1/0 |  | 0 |  | 0 | [13 empty] | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0% |  | 0.86% | 5.83% | 6.7791 | 5.893%
3 | 1 | 3/0 |  | 0 |  | 0 | [13 empty] | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0% |  | 0.72% | 6.02% | 8.3611 | 6.063%
4 | 2 | 350 |  | 0 |  | 0 | [13 empty] | 2500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0% |  | 0.67% | 5.86% | 8.7463 | 5.898%
5 | 3 | 500 |  | 0 |  | 0 | [13 empty] | 3000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0% |  | 0.77% | 5.77% | 7.4935 | 5.821%
6 | 4 | 1000 |  | 0 |  | 0 | [13 empty] | Locked Rotor Current | [21 empty] | 0.77% | 5.79% | 7.5195 | 5.841%
[20 empty] | @208V | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
[20 empty] | @480V | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
1 Phase
Trans
(kVA)
25
50
75
100
[20 empty] | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE |  |  | Three Phase Motor Data |  | Three PH Motor REF | 1 | HP | #N/A |  | OLD NUMBERS
[20 empty] | 1 | 1 |  |  | 1HP | 0.75 | 41.4096 |  |  | LOOKUP | HP | P.F. | REF
[20 empty] | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096 |  |  | 1 | 3 | 0.3 | 11 | SER 1 | 72.5424 |  | 0.3
[20 empty] | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096 |  |  | 2 | 4.5 | 0.3 | 14 | SER 2 | 72.5424 |  | 0.3
[20 empty] | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096 |  |  | 3 | 5 | 0.3 | 9 | SER 3 | 72.5424 |  | 0.3
[20 empty] | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096 |  |  | 4 | 6 | 0.3 |  | SEC 1 | 72.5424 |  | 0.3
[20 empty] | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096 |  |  | 5 | 7.5 | 0.3 |  |  | 72.5424 |  | 0.3
[20 empty] | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096 |  |  | 6 | 10 | 0.3 |  |  | 72.5424 |  | 0.3
[20 empty] | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096 |  |  | 7 | 15 | 0.3 |  |  | 72.5424 |  | 0.3
[20 empty] | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096 |  |  | 8 | 20 | 0.3 |  |  | 72.5424 |  | 0.3
[20 empty] | SINGLE PHASE LOOKUPS |  | Single PH Motor REF |  | 1 | HP | #N/A |  |  | 9 | 25 | 0.3 |  |  | 72.5424 |  | 0.3
[29 empty] | 10 | 30 | 0.3 |  |  | 72.5424 |  | 0.419
[29 empty] | 11 | 40 | 0.3 |  |  | 72.5424 |  | 0.39
[29 empty] | 12 | 50 | 0.3 |  |  | 72.5424 |  | 0.382
[29 empty] | 13 | 75 | 0.3 |  |  | 72.5424 |  | 0.349
[29 empty] | 14 | 100 | 0.3 |  |  | 72.5424 |  | 0.33
[29 empty] | 15 | 150 | 0.3 |  |  | 72.5424 |  | 0.309
[29 empty] | 16 | 200 | 0.3 |  |  | 72.5424 |  | 0.28
[29 empty] | 17 | 250 | 0.3 |  |  | 72.5424 |  | 0.251
[29 empty] | 18 | 300 | 0.3 |  |  | 72.5424 |  | 0.231
[29 empty] | 19 | 400 | 0.3 |  |  | 72.5424 |  | 0.219
[29 empty] | 20 | 500 | 0.3 |  |  | 72.5424 |  | 0.199
[29 empty] | 21 | 600 | 0.3 |  |  | 72.5424 |  | 0.178
[29 empty] | 22 | 700 | 0.3 |  |  | 72.5424 |  | 0.2
[29 empty] | 23 | 800 | 0.3 |  |  | 72.5424 |  | 0.167
[29 empty] | 24 | 900 | 0.3 |  |  | 72.5424 |  | 0.167
[29 empty] | 25 | 1000 | 0.3 |  |  | 72.5424 |  | 0.161
[29 empty] | 26 | 1200 | 0.3 |  |  | 72.5424 |  | 0.048
[29 empty] | 27 | 1500 | 0.3 |  |  | 72.5424 |  | 0.148
0.148

## UGVDROP2 (hidden)
[9 empty] | Wire Ref 3PH | 1 | [6 empty] | Ampicity | Check
| Footage | Kw | Transformer | Trans Kw |  |  |  |  | Volt Drop 3ph | 0 |  | CONDUCTOR DATA DESIGN MANUAL |  |  |  |  | 1 PH | OK
Single PH | 0 | 0 | 15 | 0 |  |  |  |  | Wire Ref 1PH | 1 | ALUMINUM CABLES OHMS / 1000 FT |  |  |  | Volt Drop | Amp Check | 3 PH | OK
Array | 0 | 0 | 15 | 0 |  |  |  |  | Volt Drop | 0 | SIZE | R | X | Z |  | 1 through 7 | 7 through 12
Three PH | 0 | 0 | 75 | 0 | [5 empty] | 1 | 2 | 0.267 | 0.0238 | 0.25067 | 0 | OK | NO
UgSerOh | 0 | 0 | [7 empty] | 2 | 1/0 | 0.168 | 0.0241 | 0.1617 | 0 | OK | NO
[9 empty] | 1 | 3 | 3/0 | 0.105 | 0.0226 | 0.10435 | 0 | OK | NO
[9 empty] | 2 | 4 | 350 | 0.0505 | 0.0215 | 0.054822 | 0 | OK | NO
PF | ANGLE |  | 1-PH = 1 | SYSTEM |  | Cable Demand | KW |  | 3 | 5 | 500 | 0.0354 | 0.0207 | 0.040883 | 0 | OK | NO
0.9 | 25.8419 |  | 3-PH = 3 | 1 |  |  | 0 |  | 4 | 6 | 1000 | 0.0177 | 0.0199 | 0.024604 | 0 | OK | NO
VOLTAGE |  |  | RUN |  | FEET |  | L-AMPS |  |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C
120 | 240 |  | 1 |  | 0 |  | 0 |  |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | 600 Volt Secondary Aluminum Cable, DB Conduit (Direct Buried)
|  |  | IF 3 PH | [7 empty] | SIZE | R@65C | R@90C | X | Z | R@90C | Z |  | (With 7-1/2 Inches Centerline to Centerline Spacing Between Conduits)
|  |  | 1 | [7 empty] | 2 | 0.31061 | 0.33653 | 0.045 | 0.32249 | 0.2052 | 0.2043 |  | Cable Size | Conduit | Number of | Number of Runs
[11 empty] | 1 | 0.24432 | 0.26471 | 0.046 | 0.25829 | 0.1623 | 0.16612 |  | Size | Size | Conductors | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Single-Phase Transformers |  |  |  | Three-Phase Transformers | [6 empty] | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.2094 | 0.1334 | 0.13924 |  | 1000 | 5"DB | 3-1/C | 605 | 1104 | 1527 | 1892 | 2335 | 2526 | 2821 | 3080 | 3339 | 3550 | 3707 | 3828
[11 empty] | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.16944 | 0.1028 | 0.11126 |  | 500 | 4"DB | 3-1/C | 397 | 736 | 1029 | 1288 | 1595 | 1746 | 1953 | 2144 | 2313 | 2470 | 2607 | 2712
kVA |  | 15 |  | kVA |  | 75 |  |  |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.13724 | 0.0825 | 0.092557 |  | 350 | 3"DB | 2-1/C | 318 | 600 | 852 | 1076 | 1285 | 1482 | 1673 | 1840 | 2016 | 2160 | 2266 | 2376
Percentage Load |  | 0% |  | Percentage Load |  | N/A |  |  |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.11354 | 0.0653 | 0.076641 |  | 350 | 3"DB | 3-1/C | 313 | 586 | 822 | 1036 | 1230 | 1416 | 1589 | 1760 | 1908 | 2040 | 2145 | 2232
%Transformer Volt Drop |  | 0 |  | %Transformer Volt Drop |  | 0 |  |  |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.098578 | 0.0552 | 0.067551 |  | 3/0 | 2"DB | 2-1/C | 202 | 386 | 552 | 704 | 875 | 984 | 1113 | 1232 | 1250 | 1440 | 1518 | 1608
Load on Transformer |  | 0 | KW |  |  | 0 | KW |  |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075795 | 0.0404 | 0.053796 |  | 3/0 | 3"DB | 3-1/C | 199 | 376 | 534 | 676 | 810 | 936 | 1057 | 1160 | 1269 | 1350 | 1419 | 1500
[11 empty] | 500 | 0.042235 | 0.04576 | 0.039 | 0.058184 | 0.0289 | 0.04301 |  | 1/0 | 2"DB | 2-1/C | 152 | 292 | 420 | 536 | 645 | 750 | 854 | 944 | 1044 | 1130 | 1188 | 1248
[11 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.043965 | 0.0199 | 0.034474 |  | #2 | 2"DB | 2-1/C | 113 | 218 | 315 | 404 | 490 | 570 | 651 | 720 | 792 | 860 | 913 | 960
[11 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.037873 | 0.0157 | 0.030258 |  | #8 | 1"DB | 1/C | 47 | 92 | 135 | 176 | 215 | 252 | 287 | 320 | 306 | 380 | 407 | 432
Ampacity OK |  | ALUMINUM CABLES |  |  |  | COPPER CABLES
Yes or No | Yes or No |  |  |  | TRANS. + CABLE |  |  | TRANS. + CABLE |  |  |  | 0.023 | 0.024115 |  | 0.077 | 0.080732
1-7 Runs | 8-12 Runs | SIZE | V - DROP | % DROP | %V-DROP | V - DROP | % DROP | V-DROP
OK | NO | 2 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Single Phase Padmount Transformer Size
|  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | kVA
OK | NO | 1/0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Percentage | 15 | 25 | Number of Runs 1: 50; Number of Runs 2: 75; Number of Runs 3: 100; Number of Runs 4: 167; Number of Runs 5: Under 50% Loading; Number of Runs 8: Select a larger Transformer
|  | 2/0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 50% | 1 | 1 | Number of Runs 1: 1; Number of Runs 2: 0.9; Number of Runs 3: 0.9; Number of Runs 4: 1; Number of Runs 6: 0
OK | NO | 3/0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 60% | 1.2 | 1.2 | Number of Runs 1: 1.2; Number of Runs 2: 1.1; Number of Runs 3: 1; Number of Runs 4: 1.2; Number of Runs 5: Over 50% Loading
|  | 4/0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 70% | 1.5 | 1.4 | Number of Runs 1: 1.4; Number of Runs 2: 1.3; Number of Runs 3: 1.2; Number of Runs 4: 1.4; Number of Runs 6: #N/A
|  | 250 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 50 |  | 80% | 1.7 | 1.6 | Number of Runs 1: 1.6; Number of Runs 2: 1.5; Number of Runs 3: 1.4; Number of Runs 4: 1.6
OK | NO | 350 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 90% | 1.9 | 1.8 | Number of Runs 1: 1.8; Number of Runs 2: 1.6; Number of Runs 3: 1.6; Number of Runs 4: 1.8
OK | NO | 500 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | #VALUE! |  | 100% | 2.1 | 2 | Number of Runs 1: 1.8; Number of Runs 2: 1.8; Number of Runs 3: 1.7; Number of Runs 4: 2
|  | 750 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 60% |  | 110% | 2.3 | 2.2 | Number of Runs 1: 2; Number of Runs 2: 2; Number of Runs 3: 1.9; Number of Runs 4: 2.2
OK | NO | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 |  | 120% | 2.5 | 2.4 | Number of Runs 1: 2.2; Number of Runs 2: 2.2; Number of Runs 3: 2.1; Number of Runs 4: 2.4
[17 empty] | 0 |  | 130% | 2.7 | 2.6 | Number of Runs 1: 2.4; Number of Runs 2: 2.4; Number of Runs 3: 2.3; Number of Runs 4: 2.6
[19 empty] | 140% | 2.9 | 2.8 | Number of Runs 1: 2.6; Number of Runs 2: 2.5; Number of Runs 3: 2.4; Number of Runs 4: 2.9
[17 empty] | 1.35 |  | 150% | 3.1 | 3 | Number of Runs 1: 2.8; Number of Runs 2: 2.7; Number of Runs 3: 2.6; Number of Runs 4: 3.1
[17 empty] | 1 |  | 160% | 3.3 | 3.2 | Number of Runs 1: 2.9; Number of Runs 2: 2.9; Number of Runs 3: 2.8; Number of Runs 4: 3.3
Number of Runs | [16 empty] | 50kVA |  | 170% | 3.5 | 3.4 | Number of Runs 1: 3; Number of Runs 2: 3.1; Number of Runs 3: 3.3; Number of Runs 4: 3.6
1 | [16 empty] | 70%
2 | [16 empty] | #N/A |  | 120/208V Three-Phase Padmount Transformer Size
3 | [18 empty] | Transformer | Kva
4 | [18 empty] | Loading | 45 | 75 | Number of Runs 1: 150; Number of Runs 2: 225; Number of Runs 3: 300; Number of Runs 4: 500; Number of Runs 5: 750; Number of Runs 6: 1000
5 | [18 empty] | 50% | 1.3 | 1.13 | Number of Runs 1: 0.89; Number of Runs 2: 0.91; Number of Runs 3: 0.98; Number of Runs 4: 1.54; Number of Runs 5: 2.03; Number of Runs 6: 1.9
6 | [18 empty] | 60% | 1.6 | 1.35 | Number of Runs 1: 1.07; Number of Runs 2: 1.1; Number of Runs 3: 1.17; Number of Runs 4: 1.8; Number of Runs 5: 2.43; Number of Runs 6: 2.33
7 | [18 empty] | 70% | 1.8 | 1.58 | Number of Runs 1: 1.2; Number of Runs 2: 1.3; Number of Runs 3: 1.37; Number of Runs 4: 2.1; Number of Runs 5: 2.84; Number of Runs 6: 2.72
8 | [18 empty] | 80% | 2.1 | 1.81 | Number of Runs 1: 1.43; Number of Runs 2: 1.46; Number of Runs 3: 1.56; Number of Runs 4: 2.4; Number of Runs 5: 3.2; Number of Runs 6: 3
9 | [18 empty] | 90% | 2.4 | 2.03 | Number of Runs 1: 1.6; Number of Runs 2: 1.64; Number of Runs 3: 1.76; Number of Runs 4: 2.7; Number of Runs 5: 3.6; Number of Runs 6: 3.4
10 | [18 empty] | 100% | 2.6 | 2.26 | Number of Runs 1: 1.78; Number of Runs 2: 1.83; Number of Runs 3: 1.9; Number of Runs 4: 3; Number of Runs 5: 4; Number of Runs 6: 3.8
11 | [18 empty] | 110% | 2.9 | 2.48 | Number of Runs 1: 1.96; Number of Runs 2: 2.01; Number of Runs 3: 2.1; Number of Runs 4: 3.3; Number of Runs 5: 4.3; Number of Runs 6: 4.2
12 | [18 empty] | 120% | 3.2 | 2.71 | Number of Runs 1: 2.14; Number of Runs 2: 2.2; Number of Runs 3: 2.3; Number of Runs 4: 3.6; Number of Runs 5: 4.7; Number of Runs 6: 4.6
[19 empty] | 130% | 3.4 | 2.94 | Number of Runs 1: 2.39; Number of Runs 2: 2.49; Number of Runs 3: 2.72; Number of Runs 4: 4; Number of Runs 5: 5.4; Number of Runs 6: 5.2
[19 empty] | 140% | 3.7 | 3.16 | Number of Runs 1: 2.57; Number of Runs 2: 2.68; Number of Runs 3: 2.93; Number of Runs 4: 4.44; Number of Runs 5: 5.9; Number of Runs 6: 5.6
[19 empty] | 150% | 4 | 3.69 | Number of Runs 1: 2.91; Number of Runs 2: 3.07; Number of Runs 3: 3.37; Number of Runs 4: 5; Number of Runs 5: 6.8; Number of Runs 6: 6.5
277/480V Three-Phase Padmount Transformer Size
[19 empty] | Transformer | Kva
[19 empty] | Loading | 75 | 150 | 225 | 300 | 500 | 750 | 1000 | 1500 | 2000 | 2500 | 3000
[19 empty] | 50% | 1.07 | 0.92 | 0.72 | 0.96 | 0.93 | 1.93 | 1.9 | 1.9 | 1.8 | 1.8 | 1.9
[19 empty] | 60% | 1.29 | 1.1 | 0.87 | 1.15 | 1.12 | 2.32 | 2.34 | 2.34 | 2.2 | 2.2 | 2.2
[19 empty] | 70% | 1.5 | 1.3 | 1.01 | 1.3 | 1.3 | 2.6 | 2.73 | 2.6 | 2.63 | 2.6 | 2.6
[19 empty] | 80% | 1.72 | 1.47 | 1.16 | 1.54 | 1.49 | 3 | 3 | 3 | 2.9 | 3.04 | 3
[19 empty] | 90% | 1.93 | 1.65 | 1.3 | 1.73 | 1.68 | 3.4 | 3.4 | 3.4 | 3.3 | 3.3 | 3.3
[19 empty] | 100% | 2.1 | 1.84 | 1.4 | 1.92 | 1.86 | 3.8 | 3.8 | 3.8 | 3.7 | 3.7 | 3.7
[19 empty] | 110% | 2.36 | 2.02 | 1.59 | 2.11 | 2 | 4.1 | 4.2 | 4.2 | 4 | 4.1 | 4.1
Transformer | Single Ph |  | Volt Drop at 100 % | [15 empty] | 120% | 2.58 | 2.21 | 1.73 | 2.31 | 2.24 | 4.5 | 4.6 | 4.5 | 4.4 | 4.4 | 4.4
Ref Cell | 1 | [17 empty] | 130% | 2.79 | 2.5 | 1.88 | 2.6 | 2.5 | 5.2 | 5.2 | 5.3 | 5.1 | 5.2 | 5.2
1 | 15 KVA | 15 | 2.1 | [15 empty] | 140% | 3.01 | 2.6 | 2.1 | 2.8 | 2.7 | 5.6 | 5.6 | 5.7 | 5.5 | 5.6 | 5.7
2 | 25 KVA | 25 | 2 | [15 empty] | 150% | 3.5 | 3 | 2.4 | 3.3 | 3.1 | 6.4 | 6.5 | 6.5 | 6.3 | 6.4 | 6.5
3 | 50 KVA | 50 | 2.5
4 | 75 KVA | 75 | 2.4
5 | 100 KVA | 100 | 2.9
6 | 167 KVA | 167 | 2.8
2

## UGFLCKER2 (hidden)
[36 empty] | 15 | 2.1 | 1.7 | 1.2 | updated 17th Feb. 2000 with table 5 of 5413.7
[36 empty] | 25 | 2 | 1.6 | 1.2
[36 empty] | 50 | 2.1 | 1.3 | 1.7
[36 empty] | 75 | 2 | 1.1 | 1.8 | 1.051 | 1.751
[36 empty] | 100 | 2.2 | 1.1 | 1.9
[19 empty] | LRC VALUES (updated 5 FEB 1998) | [15 empty] | Single Phase kVA | 167 | 2.3 | 1.1 | 2
[20 empty] | SINGLE-PHASE MOTOR SIZES IN HP | [15 empty] | 45 | 2.7153 | 1.91 | 1.93
[19 empty] | VOLTAGE | 1 | 1.5 | 2 | [13 empty] | 75 | 2.2888 | 1.72 | 1.51 | 1.62 | 1.46
[19 empty] | 120 | 46 | 69 | 92 | [13 empty] | 150 | 1.916 | 1.14 | 1.54
[36 empty] | 225 | 1.9462 | 1.19 | 1.54
[13 empty] | CONDUCTOR DATA DESIGN MANUAL | [22 empty] | 300 | 2.2897 | 1.02 | 2.05
PF |  | ANGLE |  | 1-PH = 1 |  | # OF PHASES | HP | 1Ph-LRC | 1Ph-XKMR% | R |  | ALUMINUM CABLES OHMS / 1000 FT | [23 empty] | 500 | 4.5034 | 0.81 | 4.43
0.75 |  | 41.4096 |  | 3-PH = 3 |  | 1 | 1 | 27 | 0.89369 | 1.7 | 1-Ph | SIZE | R | X | Z | L-AMPS |  |  | LRC VALUES (updated 5 FEB 1998) | [16 empty] | 750 | 6.0451 | 0.95 | 5.97
[8 empty] | 3Ph-LRC |  | #N/A | 3-Ph | 2 | 0.267 | 0.0238 | 0.21599 | 27 |  |  |  | SINGLE-PHASE MOTOR SIZES IN HORSE POWER | [15 empty] | 1000 | 5.82 | 0.9 | 5.75
[8 empty] | n/a |  | X |  | 1/0 | 0.168 | 0.0241 | 0.14194 |  |  |  | VOLTAGE | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 10 | [7 empty] | 1500 | 0 | 0 | 0
VOLTAGE |  |  |  | RUN |  | FEET | KW | XFMR KVA | 3Ph-XFMR % | 1.2 | 1-Ph | 3/0 | 0.105 | 0.0226 | 0.093698 |  |  |  | 240 | 27 | 34 | 46 | 69 | 103 | 115 | 140 | 175 | 218 | [7 empty] | 2000 | 0 | 0 | 0
120 |  | 240 |  | 1 |  | 0 | 4.86 | 15 | 0 | #N/A | 3-Ph | 350 | 0.0505 | 0.0215 | 0.052096 | [20 empty] | 2500 | 0 | 0 | 0
[12 empty] | 500 | 0.0354 | 0.0207 | 0.040242 | [20 empty] | 3000 | 0 | 0 | 0
ALUMINUM CABLES | [6 empty] | COPPER CABLES | [27 empty] | Three Phase kVA | Three Phase kVA | Z% | R% | X%
|  | CABLE |  | CABLE |  | *TOTAL% | CABLE | CABLE | *TOTAL% |  |  | 1000 | 0.0177 | 0.0199 | 0.026438 | [20 empty] | updated 17th Feb. 2000 with table 9 of 5413.7
SIZE |  | (VOLTS) |  | ( % ) |  | FLICKER | (VOLTS) | ( % ) | FLICKER |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C | [6 empty] | LRC VALUES (updated 31dec1997)
2 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | MOTOR SIZES IN HORSE POWER
1 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | SIZE | R@65C | R@90C | X | Z | R@90C | Z | VOLTAGE | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200
1/0 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 2 | 0.31061 | 0.33653 | 0.045 | 0.28216 | 0.2052 | 0.18366 | 208 | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
2/0 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 1 | 0.24432 | 0.26471 | 0.046 | 0.22896 | 0.1623 | 0.15215 | 240 | 64 | 85 | 92 | 106 | 127 | 162 | 232 | 290 | 365 | 435 | 580 | 725 | 1085 | 1450 | 2170
3/0 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.18762 | 0.1334 | 0.12915 | 480 | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
4/0 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.15403 | 0.1028 | 0.10554
250 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.12689 | 0.0825 | 0.089655
350 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.10684 | 0.0653 | 0.076094
500 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.094374 | 0.0552 | 0.068519
750 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075091 | 0.0404 | 0.056758 |  | 3 Phase | Three-Phase Motor (Sized in HP) | [15 empty] | Transformer Data |  | X/R
1000 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 500 | 0.042235 | 0.04576 | 0.039 | 0.060116 | 0.0289 | 0.047471 |  | Trans | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200 | R | X | Ratio | Z%
[12 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.047969 | 0.0199 | 0.04006 |  | 45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.0191 | 0.0193 | 1.0105 | 2.715%
[12 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.042594 | 0.0157 | 0.036248 |  | 75 | 0.66522 | 0.88072 | 0.95567 | 1.0962 | 1.3117 | 1.6771 | 2.4079 | 3.0076 | 3.7852 | 4.5066 | 6.0057 | 7.5142 | 11.2432 | 15.019 | 22.4864 | 30.0474 | 0.0172 | 0.0151 | 0.87791 | 2.289%
WITH REDUCED LRC TO 770A OR 50HP | [6 empty] | *TOTAL FLICKER = CABLE (%) + XMFR (%) | [12 empty] | 150 | 0.3078 | 0.40751 | 0.44219 | 0.54094 | 0.60693 | 0.776 | 1.1141 | 1.3916 | 1.7514 | 2.0852 | 2.7789 | 3.4768 | 5.2022 | 6.9493 | 10.4045 | 13.903 | 0.0114 | 0.0154 | 1.3509 | 1.916%
[13 empty] | 0.023 | 0.024115 |  | 0.077 | 0.080732 |  |  | 225 | 0.20691 | 0.27393 | 0.29724 | 0.34096 | 0.40798 | 0.52163 | 0.74894 | 0.93544 | 1.1773 | 1.4017 | 1.868 | 2.3372 | 3.497 | 4.6714 | 6.994 | 9.3457 | 0.0119 | 0.0154 | 1.2941 | 1.946%
[20 empty] | 300 | 0.19214 | 0.25438 | 0.27603 | 0.31663 | 0.37887 | 0.48441 | 0.69549 | 0.86869 | 1.0933 | 1.3017 | 1.7347 | 2.1704 | 3.2474 | 4.338 | 6.4949 | 8.6788 | 0.0102 | 0.0205 | 2.0098 | 2.29%
Lookup Value |  |  | 1ph | 0 | 3ph | 0 | [13 empty] | 500 | 0.22773 | 0.3015 | 0.32716 | 0.37527 | 0.44904 | 0.57413 | 0.82432 | 1.0296 | 1.2958 | 1.5428 | 2.056 | 2.5724 | 3.8489 | 5.1415 | 7.6979 | 10.2863 | 0.0081 | 0.0443 | 5.4691 | 4.503%
Lookup |  | Wire |  | Volatge Drop |  | % Volatge Drop | [13 empty] | 750 | 0.20315 | 0.26896 | 0.29185 | 0.33476 | 0.40057 | 0.51216 | 0.73534 | 0.91846 | 1.1559 | 1.3763 | 1.8341 | 2.2947 | 3.4335 | 4.5866 | 6.867 | 9.176 | 0.0095 | 0.0597 | 6.2842 | 6.045%
1 |  | 2 |  | 0 |  | 0 | [13 empty] | 1000 | 0.14663 | 0.19413 | 0.21065 | 0.24163 | 0.28913 | 0.36968 | 0.53076 | 0.66294 | 0.83435 | 0.99337 | 1.3238 | 1.6563 | 2.4783 | 3.3106 | 4.9565 | 6.6232 | 0.009 | 0.0575 | 6.3889 | 5.82%
2 |  | 1/0 |  | 0 |  | 0 | [13 empty] | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
3 | 1 | 3/0 |  | 0 |  | 0 | [13 empty] | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
4 | 2 | 350 |  | 0 |  | 0 |  |  |  | 0 | 0 | [8 empty] | 2500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
5 | 3 | 500 |  | 0 |  | 0 |  |  |  | 0 | 0 | [8 empty] | 3000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
6 | 4 | 1000 |  | 0 |  | 0 | [13 empty] | Locked Rotor Current
[20 empty] | @208V | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
[20 empty] | @480V | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
1 Phase
Trans
(kVA)
25
50
75
100
[20 empty] | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE |  |  | Three Phase Motor Data |  | Three PH Motor REF | 1 | HP | #N/A
[20 empty] | 1 | 1 |  |  | 1HP | 0.75 | 41.4096 |  |  | LOOKUP | HP | P.F. | REF
[20 empty] | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096 |  |  | 1 | 3 | 0.3 | 11 | SER 1 | 72.5424
[20 empty] | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096 |  |  | 2 | 4.5 | 0.3 | 14 | SER 2 | 72.5424
[20 empty] | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096 |  |  | 3 | 5 | 0.3 | 9 | SER 3 | 72.5424
[20 empty] | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096 |  |  | 4 | 6 | 0.3 |  | SEC 1 | 72.5424
[20 empty] | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096 |  |  | 5 | 7.5 | 0.3 |  |  | 72.5424
[20 empty] | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096 |  |  | 6 | 10 | 0.3 |  |  | 72.5424
[20 empty] | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096 |  |  | 7 | 15 | 0.3 |  |  | 72.5424
[20 empty] | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096 |  |  | 8 | 20 | 0.3 |  |  | 72.5424
[20 empty] | SINGLE PHASE LOOKUPS |  | Single PH Motor REF |  | 1 | HP | #N/A |  |  | 9 | 25 | 0.3 |  |  | 72.5424
[29 empty] | 10 | 30 | 0.3 |  |  | 72.5424
[29 empty] | 11 | 40 | 0.3 |  |  | 72.5424
[29 empty] | 12 | 50 | 0.3 |  |  | 72.5424
[29 empty] | 13 | 75 | 0.3 |  |  | 72.5424
[29 empty] | 14 | 100 | 0.3 |  |  | 72.5424
[29 empty] | 15 | 150 | 0.3 |  |  | 72.5424
[29 empty] | 16 | 200 | 0.3 |  |  | 72.5424
[29 empty] | 17 | 250 | 0.3 |  |  | 72.5424
[29 empty] | 18 | 300 | 0.3 |  |  | 72.5424
[29 empty] | 19 | 400 | 0.3 |  |  | 72.5424
[29 empty] | 20 | 500 | 0.3 |  |  | 72.5424
[29 empty] | 21 | 600 | 0.3 |  |  | 72.5424
[29 empty] | 22 | 700 | 0.3 |  |  | 72.5424
[29 empty] | 23 | 800 | 0.3 |  |  | 72.5424
[29 empty] | 24 | 900 | 0.3 |  |  | 72.5424
[29 empty] | 25 | 1000 | 0.3 |  |  | 72.5424
[29 empty] | 26 | 1200 | 0.3 |  |  | 72.5424
[29 empty] | 27 | 1500 | 0.3 |  |  | 72.5424

## UGVDROP3 (hidden)
Tap note
[9 empty] | Taps | Rel Cell | 3 | Value
[9 empty] | 1 | 5 | -5 | 0 | 45 kva note
[9 empty] | 2 | 2.5 | -2.5
[9 empty] | 3 | 0 | 0
[9 empty] | 4 | -2.5 | 2.5 |  | Per Design Manual 3Ph Power Factor to be .85
[9 empty] | 5 | -5 | 5 |  | Select Basic Info to change Factor.
[9 empty] | Wire Ref 3PH | 1 | [6 empty] | Ampicity | Check
| Footage | kW | Transformer | Trans kW |  |  |  |  | Volt Drop 3ph | 0 |  | CONDUCTOR DATA DESIGN MANUAL |  |  |  |  | 1 pH | OK
Single PH | 0 | 0 | 15 | 0 |  |  |  |  | Wire Ref 1PH | 1 | ALUMINUM CABLES OHMS / 1000 FT |  |  |  | Volt Drop | Amp Check | 3 PH | OK
Array | 0 | 0 | 15 | 0 |  |  |  |  | Volt Drop | 0 | SIZE | R | X | Z |  | 1 through 7 | 7 through 12
Three PH | 0 | 0 | 75 | 0 | [5 empty] | 1 | 2 | 0.267 | 0.0238 | 0.25067 | 0 | OK | NO
UgSerOh | 0 | 0 | [7 empty] | 2 | 1/0 | 0.168 | 0.0241 | 0.1617 | 0 | OK | NO
[9 empty] | 1 | 3 | 3/0 | 0.105 | 0.0226 | 0.10435 | 0 | OK | NO
[9 empty] | 2 | 4 | 350 | 0.0505 | 0.0215 | 0.054822 | 0 | OK | NO
PF | ANGLE |  | 1-PH = 1 | SYSTEM |  | Cable Demand | KW |  | 3 | 5 | 500 | 0.0354 | 0.0207 | 0.040883 | 0 | OK | NO
0.9 | 25.8419 |  | 3-PH = 3 | 1 |  |  | 0 |  | 4 | 6 | 1000 | 0.0177 | 0.0199 | 0.024604 | 0 | OK | NO
VOLTAGE |  |  | RUN |  | FEET |  | L-AMPS |  |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C
120 | 240 |  | 1 |  | 0 |  | 0 |  |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | 600 Volt Secondary Aluminum Cable, DB Conduit (Direct Buried)
|  |  | IF 3 PH | [7 empty] | SIZE | R@65C | R@90C | X | Z | R@90C | Z |  | (With 7-1/2 Inches Centerline to Centerline Spacing Between Conduits)
|  |  | 1 | [7 empty] | 2 | 0.31061 | 0.33653 | 0.045 | 0.32249 | 0.2052 | 0.2043 |  | Cable Size | Conduit | Number of | Number of Runs
[11 empty] | 1 | 0.24432 | 0.26471 | 0.046 | 0.25829 | 0.1623 | 0.16612 |  | Size | Size | Conductors | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Single-Phase Transformers |  |  |  | Three-Phase Transformers | [6 empty] | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.2094 | 0.1334 | 0.13924 |  | 1000 | 5"DB | 3-1/C | 605 | 1104 | 1527 | 1892 | 2335 | 2526 | 2821 | 3080 | 3339 | 3550 | 3707 | 3828
[11 empty] | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.16944 | 0.1028 | 0.11126 |  | 500 | 4"DB | 3-1/C | 397 | 736 | 1029 | 1288 | 1595 | 1746 | 1953 | 2144 | 2313 | 2470 | 2607 | 2712
KVA |  | 15 |  | KVA |  | 75 |  |  |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.13724 | 0.0825 | 0.092557 |  | 350 | 3"DB | 2-1/C | 318 | 600 | 852 | 1076 | 1285 | 1482 | 1673 | 1840 | 2016 | 2160 | 2266 | 2376
Percentage Load |  | 0% |  | Percentage Load |  | N/A |  |  |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.11354 | 0.0653 | 0.076641 |  | 350 | 3"DB | 3-1/C | 313 | 586 | 822 | 1036 | 1230 | 1416 | 1589 | 1760 | 1908 | 2040 | 2145 | 2232
%Transformer Volt Drop |  | #N/A |  | %Transformer Volt Drop |  | 0 |  |  |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.098578 | 0.0552 | 0.067551 |  | 3/0 | 2"DB | 2-1/C | 202 | 386 | 552 | 704 | 875 | 984 | 1113 | 1232 | 1250 | 1440 | 1518 | 1608
Load on Transformer |  | 0 | KW |  |  | 0 | KW |  |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075795 | 0.0404 | 0.053796 |  | 3/0 | 3"DB | 3-1/C | 199 | 376 | 534 | 676 | 810 | 936 | 1057 | 1160 | 1269 | 1350 | 1419 | 1500
[11 empty] | 500 | 0.042235 | 0.04576 | 0.039 | 0.058184 | 0.0289 | 0.04301 |  | 1/0 | 2"DB | 2-1/C | 152 | 292 | 420 | 536 | 645 | 750 | 854 | 944 | 1044 | 1130 | 1188 | 1248
[11 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.043965 | 0.0199 | 0.034474 |  | #2 | 2"DB | 2-1/C | 113 | 218 | 315 | 404 | 490 | 570 | 651 | 720 | 792 | 860 | 913 | 960
[11 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.037873 | 0.0157 | 0.030258 |  | #8 | 1"DB | 1/C | 47 | 92 | 135 | 176 | 215 | 252 | 287 | 320 | 306 | 380 | 407 | 432
Ampacity OK |  | ALUMINUM CABLES |  |  |  | COPPER CABLES
Yes or No | Yes or No |  |  |  | TRANS. + CABLE |  |  | TRANS. + CABLE |  |  |  | 0.023 | 0.024115 |  | 0.077 | 0.080732
1-7 Runs | 8-12 Runs | SIZE | V - DROP | % DROP | %V-DROP | V - DROP | % DROP | V-DROP
OK | NO | 2 | 0 | 0 | #N/A | 0 | 0 | #N/A | [10 empty] | Single Phase Padmount Transformer Size
|  | 1 | 0 | 0 | #N/A | 0 | 0 | #N/A | [11 empty] | kVA
OK | NO | 1/0 | 0 | 0 | #N/A | 0 | 0 | #N/A | [10 empty] | Percentage | 15 | 25 | Number of Runs 1: 50; Number of Runs 2: 75; Number of Runs 3: 100; Number of Runs 4: 167; Number of Runs 5: Under 50% Loading
|  | 2/0 | 0 | 0 | #N/A | 0 | 0 | #N/A | [10 empty] | 50% | 1 | 1 | Number of Runs 1: 1; Number of Runs 2: 0.9; Number of Runs 3: 0.9; Number of Runs 4: 1; Number of Runs 6: #N/A
OK | NO | 3/0 | 0 | 0 | #N/A | 0 | 0 | #N/A | [10 empty] | 60% | 1.2 | 1.2 | Number of Runs 1: 1.2; Number of Runs 2: 1.1; Number of Runs 3: 1; Number of Runs 4: 1.2; Number of Runs 5: Over 50% Loading
|  | 4/0 | 0 | 0 | #N/A | 0 | 0 | #N/A | [10 empty] | 70% | 1.5 | 1.4 | Number of Runs 1: 1.4; Number of Runs 2: 1.3; Number of Runs 3: 1.2; Number of Runs 4: 1.4; Number of Runs 6: #N/A
|  | 250 | 0 | 0 | #N/A | 0 | 0 | #N/A | [8 empty] | 50 |  | 80% | 1.7 | 1.6 | Number of Runs 1: 1.6; Number of Runs 2: 1.5; Number of Runs 3: 1.4; Number of Runs 4: 1.6
OK | NO | 350 | 0 | 0 | #N/A | 0 | 0 | #N/A | [10 empty] | 90% | 1.9 | 1.8 | Number of Runs 1: 1.8; Number of Runs 2: 1.6; Number of Runs 3: 1.6; Number of Runs 4: 1.8
OK | NO | 500 | 0 | 0 | #N/A | 0 | 0 | #N/A | [8 empty] | #VALUE! |  | 100% | 2.1 | 2 | Number of Runs 1: 1.8; Number of Runs 2: 1.8; Number of Runs 3: 1.7; Number of Runs 4: 2
|  | 750 | 0 | 0 | #N/A | 0 | 0 | #N/A | [8 empty] | 60% |  | 110% | 2.3 | 2.2 | Number of Runs 1: 2; Number of Runs 2: 2; Number of Runs 3: 1.9; Number of Runs 4: 2.2
OK | NO | 1000 | 0 | 0 | #N/A | 0 | 0 | #N/A | [8 empty] | 0 |  | 120% | 2.5 | 2.4 | Number of Runs 1: 2.2; Number of Runs 2: 2.2; Number of Runs 3: 2.1; Number of Runs 4: 2.4
[17 empty] | 0 |  | 130% | 2.7 | 2.6 | Number of Runs 1: 2.4; Number of Runs 2: 2.4; Number of Runs 3: 2.3; Number of Runs 4: 2.6
[19 empty] | 140% | 2.9 | 2.8 | Number of Runs 1: 2.6; Number of Runs 2: 2.5; Number of Runs 3: 2.4; Number of Runs 4: 2.9
[17 empty] | 1.35 |  | 150% | 3.1 | 3 | Number of Runs 1: 2.8; Number of Runs 2: 2.7; Number of Runs 3: 2.6; Number of Runs 4: 3.1
[17 empty] | 1 |  | 160% | 3.3 | 3.2 | Number of Runs 1: 2.9; Number of Runs 2: 2.9; Number of Runs 3: 2.8; Number of Runs 4: 3.3
Number of Runs | [16 empty] | 50kVA |  | 170% | 3.5 | 3.4 | Number of Runs 1: 3; Number of Runs 2: 3.1; Number of Runs 3: 3.3; Number of Runs 4: 3.6
1 | [16 empty] | 70%
2 | [16 empty] | #N/A |  | 120/208V Three-Phase Padmount Transformer Size
3 | [18 empty] | Transformer | Kva
4 | [18 empty] | Loading | 45 | 75 | Number of Runs 1: 150; Number of Runs 2: 225; Number of Runs 3: 300; Number of Runs 4: 500; Number of Runs 5: 750; Number of Runs 6: 1000
5 | [18 empty] | 50% | 1.3 | 1.13 | Number of Runs 1: 0.89; Number of Runs 2: 0.91; Number of Runs 3: 0.98; Number of Runs 4: 1.54; Number of Runs 5: 2.03; Number of Runs 6: 1.9
6 | [18 empty] | 60% | 1.6 | 1.35 | Number of Runs 1: 1.07; Number of Runs 2: 1.1; Number of Runs 3: 1.17; Number of Runs 4: 1.8; Number of Runs 5: 2.43; Number of Runs 6: 2.33
7 | [18 empty] | 70% | 1.8 | 1.58 | Number of Runs 1: 1.2; Number of Runs 2: 1.3; Number of Runs 3: 1.37; Number of Runs 4: 2.1; Number of Runs 5: 2.84; Number of Runs 6: 2.72
8 | [18 empty] | 80% | 2.1 | 1.81 | Number of Runs 1: 1.43; Number of Runs 2: 1.46; Number of Runs 3: 1.56; Number of Runs 4: 2.4; Number of Runs 5: 3.2; Number of Runs 6: 3
9 | [18 empty] | 90% | 2.4 | 2.03 | Number of Runs 1: 1.6; Number of Runs 2: 1.64; Number of Runs 3: 1.76; Number of Runs 4: 2.7; Number of Runs 5: 3.6; Number of Runs 6: 3.4
10 | [18 empty] | 100% | 2.6 | 2.26 | Number of Runs 1: 1.78; Number of Runs 2: 1.83; Number of Runs 3: 1.9; Number of Runs 4: 3; Number of Runs 5: 4; Number of Runs 6: 3.8
11 | [18 empty] | 110% | 2.9 | 2.48 | Number of Runs 1: 1.96; Number of Runs 2: 2.01; Number of Runs 3: 2.1; Number of Runs 4: 3.3; Number of Runs 5: 4.3; Number of Runs 6: 4.2
12 | [18 empty] | 120% | 3.2 | 2.71 | Number of Runs 1: 2.14; Number of Runs 2: 2.2; Number of Runs 3: 2.3; Number of Runs 4: 3.6; Number of Runs 5: 4.7; Number of Runs 6: 4.6
[19 empty] | 130% | 3.4 | 2.94 | Number of Runs 1: 2.39; Number of Runs 2: 2.49; Number of Runs 3: 2.72; Number of Runs 4: 4; Number of Runs 5: 5.4; Number of Runs 6: 5.2
[19 empty] | 140% | 3.7 | 3.16 | Number of Runs 1: 2.57; Number of Runs 2: 2.68; Number of Runs 3: 2.93; Number of Runs 4: 4.44; Number of Runs 5: 5.9; Number of Runs 6: 5.6
[19 empty] | 150% | 4 | 3.69 | 2.91 | 3.07 | 3.37 | 5 | 6.8 | 6.5 | Under 50% Loading |  |  | Select a larger
[29 empty] | #VALUE! |  | Transformer
Over 50% Loading
[19 empty] | 277/480V Three-Phase Padmount Transformer Size |  |  | Number of Runs 8: 0
[19 empty] | Transformer | Kva
[19 empty] | Loading | 75 | 150 | 225 | 300 | 500 | 750 | 1000 | 1500 | 2000 | 2500 | 3000
[19 empty] | 50% | 1.07 | 0.92 | 0.72 | 0.96 | 0.93 | 1.93 | 1.9 | 1.9 | 1.8 | 1.8 | 1.9
[19 empty] | 60% | 1.29 | 1.1 | 0.87 | 1.15 | 1.12 | 2.32 | 2.34 | 2.34 | 2.2 | 2.2 | 2.2
[19 empty] | 70% | 1.5 | 1.3 | 1.01 | 1.3 | 1.3 | 2.6 | 2.73 | 2.6 | 2.63 | 2.6 | 2.6
[19 empty] | 80% | 1.72 | 1.47 | 1.16 | 1.54 | 1.49 | 3 | 3 | 3 | 2.9 | 3.04 | 3
[19 empty] | 90% | 1.93 | 1.65 | 1.3 | 1.73 | 1.68 | 3.4 | 3.4 | 3.4 | 3.3 | 3.3 | 3.3
[19 empty] | 100% | 2.1 | 1.84 | 1.4 | 1.92 | 1.86 | 3.8 | 3.8 | 3.8 | 3.7 | 3.7 | 3.7
[19 empty] | 110% | 2.36 | 2.02 | 1.59 | 2.11 | 2 | 4.1 | 4.2 | 4.2 | 4 | 4.1 | 4.1
Three Phase Transformers |  |  | REF CELL | 2 |  | Volt Drop at 100 % | [12 empty] | 120% | 2.58 | 2.21 | 1.73 | 2.31 | 2.24 | 4.5 | 4.6 | 4.5 | 4.4 | 4.4 | 4.4
[6 empty] | 208 V | 480 V | [11 empty] | 130% | 2.79 | 2.5 | 1.88 | 2.6 | 2.5 | 5.2 | 5.2 | 5.3 | 5.1 | 5.2 | 5.2
1 | 45 kVA | 45 |  |  |  | 2.6 | [12 empty] | 140% | 3.01 | 2.6 | 2.1 | 2.8 | 2.7 | 5.6 | 5.6 | 5.7 | 5.5 | 5.6 | 5.7
2 | 75 KVA | 75 |  |  |  | 2.26 | 2.1 | [11 empty] | 150% | 3.5 | 3 | 2.4 | 3.3 | 3.1 | 6.4 | 6.5 | 6.5 | 6.3 | 6.4 | 6.5
3 | 150 KVA | 150 |  |  |  | 1.78 | 1.84
4 | 225 KVA | 225 |  |  |  | 1.83 | 1.4
5 | 300 KVA | 300 |  |  |  | 1.9 | 1.92
6 | 500 KVA | 500 |  |  |  | 3 | 1.86
7 | 750 KVA | 750 |  |  |  | 4 | 3.8
8 | 1000 KVA | 1000 |  |  |  | 3.8 | 3.8
9 | 1500 KVA | 1500 |  |  |  |  | 3.8
10 | 2000 KVA | 2000 |  |  |  |  | 3.7
11 | 2500 KVA | 2500 |  |  |  |  | 3.7
12 | 3000 KVA | 3000 |  |  |  |  | 3.7
2

## UGFLCKER3 (hidden)
[36 empty] | 15 | 2.1 | 1.7 | 1.2 | updated 17th Feb. 2000 with table 5 of 5413.7
[36 empty] | 25 | 2 | 1.6 | 1.2
[36 empty] | 50 | 2.1 | 1.3 | 1.7
[36 empty] | 75 | 2 | 1.1 | 1.8 | 1.051 | 1.751
[36 empty] | 100 | 2.2 | 1.1 | 1.9
[19 empty] | LRC VALUES (updated 5 FEB 1998) | [15 empty] | Single Phase kVA | 167 | 2.3 | 1.1 | 2
[7 empty] | #N/A | [12 empty] | SINGLE-PHASE MOTOR SIZES IN HP | [15 empty] | 45 | 2.7153 | 1.91 | 1.93
[19 empty] | VOLTAGE | 1 | 1.5 | 2 | [13 empty] | 75 | 2.2888 | 1.72 | 1.51 | 1.62 | 1.46
[19 empty] | 120 | 46 | 69 | 92 | [13 empty] | 150 | 1.916 | 1.14 | 1.54
[36 empty] | 225 | 1.9462 | 1.19 | 1.54
[13 empty] | CONDUCTOR DATA DESIGN MANUAL | [22 empty] | 300 | 2.2897 | 1.02 | 2.05
PF |  | ANGLE |  | 1-PH = 1 |  | # OF PHASES | HP | 1Ph-LRC | 1Ph-XKMR% |  |  | ALUMINUM CABLES OHMS / 1000 FT | [23 empty] | 500 | 4.5034 | 0.81 | 4.43
0.75 |  | 41.4096 |  | 3-PH = 3 |  | 1 | 1 | 27 | 0.89369 | 1.7 | 1-Ph | SIZE | R | X | Z | L-AMPS |  |  | LRC VALUES (updated 5 FEB 1998) | [16 empty] | 750 | 6.0451 | 0.95 | 5.97
[8 empty] | 3Ph-LRC |  | #N/A | 3-Ph | 2 | 0.267 | 0.0238 | 0.21599 | 27 |  |  |  | SINGLE-PHASE MOTOR SIZES IN HORSE POWER | [15 empty] | 1000 | 5.82 | 0.9 | 5.75
[8 empty] | n/a |  | X |  | 1/0 | 0.168 | 0.0241 | 0.14194 |  |  |  | VOLTAGE | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 10 | [7 empty] | 1500 | 0 | 0 | 0
VOLTAGE |  |  |  | RUN |  | FEET | KW | XFMR KVA | 3Ph-XFMR % | 1.2 | 1-Ph | 3/0 | 0.105 | 0.0226 | 0.093698 |  |  |  | 240 | 27 | 34 | 46 | 69 | 103 | 115 | 140 | 175 | 218 | [7 empty] | 2000 | 0 | 0 | 0
120 |  | 240 |  | 1 |  | 0 | 4.86 | 15 | 0 | #N/A |  | 350 | 0.0505 | 0.0215 | 0.052096 | [20 empty] | 2500 | 0 | 0 | 0
[12 empty] | 500 | 0.0354 | 0.0207 | 0.040242 | [20 empty] | 3000 | 0 | 0 | 0
ALUMINUM CABLES | [6 empty] | COPPER CABLES | [27 empty] | Three Phase kVA | Three Phase kVA | Z% | R% | X%
|  | CABLE |  | CABLE |  | *TOTAL% | CABLE | CABLE | *TOTAL% |  |  | 1000 | 0.0177 | 0.0199 | 0.026438 | [20 empty] | updated 17th Feb. 2000 with table 9 of 5413.7
SIZE |  | (VOLTS) |  | ( % ) |  | FLICKER | (VOLTS) | ( % ) | FLICKER |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C | [6 empty] | LRC VALUES (updated 31dec1997)
2 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | MOTOR SIZES IN HORSE POWER
1 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | SIZE | R@65C | R@90C | X | Z | R@90C | Z | VOLTAGE | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200
1/0 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 2 | 0.31061 | 0.33653 | 0.045 | 0.28216 | 0.2052 | 0.18366 | 208 | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
2/0 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 1 | 0.24432 | 0.26471 | 0.046 | 0.22896 | 0.1623 | 0.15215 | 240 | 64 | 85 | 92 | 106 | 127 | 162 | 232 | 290 | 365 | 435 | 580 | 725 | 1085 | 1450 | 2170
3/0 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.18762 | 0.1334 | 0.12915 | 480 | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
4/0 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.15403 | 0.1028 | 0.10554
250 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.12689 | 0.0825 | 0.089655
350 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.10684 | 0.0653 | 0.076094
500 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.094374 | 0.0552 | 0.068519
750 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075091 | 0.0404 | 0.056758 |  | 3 Phase | Three-Phase Motor (Sized in HP) | [15 empty] | Transformer Data |  | X/R
1000 |  | 0 |  | 0 |  | 0.89369 | 0 | 0 | 0 |  |  | 500 | 0.042235 | 0.04576 | 0.039 | 0.060116 | 0.0289 | 0.047471 |  | Trans | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200 | R | X | Ratio | Z%
[12 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.047969 | 0.0199 | 0.04006 |  | 45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.0191 | 0.0193 | 1.0105 | 2.715%
[12 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.042594 | 0.0157 | 0.036248 |  | 75 | 0.66522 | 0.88072 | 0.95567 | 1.0962 | 1.3117 | 1.6771 | 2.4079 | 3.0076 | 3.7852 | 4.5066 | 6.0057 | 7.5142 | 11.2432 | 15.019 | 22.4864 | 30.0474 | 0.0172 | 0.0151 | 0.87791 | 2.289%
WITH REDUCED LRC TO 770A OR 50HP | [6 empty] | *TOTAL FLICKER = CABLE (%) + XMFR (%) | [12 empty] | 150 | 0.3078 | 0.40751 | 0.44219 | 0.54094 | 0.60693 | 0.776 | 1.1141 | 1.3916 | 1.7514 | 2.0852 | 2.7789 | 3.4768 | 5.2022 | 6.9493 | 10.4045 | 13.903 | 0.0114 | 0.0154 | 1.3509 | 1.916%
[13 empty] | 0.023 | 0.024115 |  | 0.077 | 0.080732 |  |  | 225 | 0.20691 | 0.27393 | 0.29724 | 0.34096 | 0.40798 | 0.52163 | 0.74894 | 0.93544 | 1.1773 | 1.4017 | 1.868 | 2.3372 | 3.497 | 4.6714 | 6.994 | 9.3457 | 0.0119 | 0.0154 | 1.2941 | 1.946%
[20 empty] | 300 | 0.19214 | 0.25438 | 0.27603 | 0.31663 | 0.37887 | 0.48441 | 0.69549 | 0.86869 | 1.0933 | 1.3017 | 1.7347 | 2.1704 | 3.2474 | 4.338 | 6.4949 | 8.6788 | 0.0102 | 0.0205 | 2.0098 | 2.29%
Lookup Value |  |  | 1ph | 0 | 3ph | 0 | [13 empty] | 500 | 0.22773 | 0.3015 | 0.32716 | 0.37527 | 0.44904 | 0.57413 | 0.82432 | 1.0296 | 1.2958 | 1.5428 | 2.056 | 2.5724 | 3.8489 | 5.1415 | 7.6979 | 10.2863 | 0.0081 | 0.0443 | 5.4691 | 4.503%
Lookup |  | Wire |  | Volatge Drop |  | % Volatge Drop | [13 empty] | 750 | 0.20315 | 0.26896 | 0.29185 | 0.33476 | 0.40057 | 0.51216 | 0.73534 | 0.91846 | 1.1559 | 1.3763 | 1.8341 | 2.2947 | 3.4335 | 4.5866 | 6.867 | 9.176 | 0.0095 | 0.0597 | 6.2842 | 6.045%
1 |  | 2 |  | 0 |  | 0 | [13 empty] | 1000 | 0.14663 | 0.19413 | 0.21065 | 0.24163 | 0.28913 | 0.36968 | 0.53076 | 0.66294 | 0.83435 | 0.99337 | 1.3238 | 1.6563 | 2.4783 | 3.3106 | 4.9565 | 6.6232 | 0.009 | 0.0575 | 6.3889 | 5.82%
2 |  | 1/0 |  | 0 |  | 0 | [13 empty] | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
3 | 1 | 3/0 |  | 0 |  | 0 | [13 empty] | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
4 | 2 | 350 |  | 0 |  | 0 | [13 empty] | 2500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
5 | 3 | 500 |  | 0 |  | 0 | [13 empty] | 3000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
6 | 4 | 1000 |  | 0 |  | 0 | [13 empty] | Locked Rotor Current
[20 empty] | @208V | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
[20 empty] | @480V | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
1 Phase
Trans
(kVA)
25
50
75
100
[20 empty] | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE |  |  | Three Phase Motor Data |  | Three PH Motor REF | 1 | HP | #N/A
[20 empty] | 1 | 1 |  |  | 1HP | 0.75 | 41.4096 |  |  | LOOKUP | HP | P.F. | REF
[20 empty] | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096 |  |  | 1 | 3 | 0.3 | 11 | SER 1 | 72.5424
[20 empty] | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096 |  |  | 2 | 4.5 | 0.3 | 14 | SER 2 | 72.5424
[20 empty] | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096 |  |  | 3 | 5 | 0.3 | 9 | SER 3 | 72.5424
[20 empty] | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096 |  |  | 4 | 6 | 0.3 |  | SEC 1 | 72.5424
[20 empty] | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096 |  |  | 5 | 7.5 | 0.3 |  |  | 72.5424
[20 empty] | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096 |  |  | 6 | 10 | 0.3 |  |  | 72.5424
[20 empty] | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096 |  |  | 7 | 15 | 0.3 |  |  | 72.5424
[20 empty] | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096 |  |  | 8 | 20 | 0.3 |  |  | 72.5424
[20 empty] | SINGLE PHASE LOOKUPS |  | Single PH Motor REF |  | 1 | HP | #N/A |  |  | 9 | 25 | 0.3 |  |  | 72.5424
[29 empty] | 10 | 30 | 0.3 |  |  | 72.5424
[29 empty] | 11 | 40 | 0.3 |  |  | 72.5424
[29 empty] | 12 | 50 | 0.3 |  |  | 72.5424
[29 empty] | 13 | 75 | 0.3 |  |  | 72.5424
[29 empty] | 14 | 100 | 0.3 |  |  | 72.5424
[29 empty] | 15 | 150 | 0.3 |  |  | 72.5424
[29 empty] | 16 | 200 | 0.3 |  |  | 72.5424
[29 empty] | 17 | 250 | 0.3 |  |  | 72.5424
[29 empty] | 18 | 300 | 0.3 |  |  | 72.5424
[29 empty] | 19 | 400 | 0.3 |  |  | 72.5424
[29 empty] | 20 | 500 | 0.3 |  |  | 72.5424
[29 empty] | 21 | 600 | 0.3 |  |  | 72.5424
[29 empty] | 22 | 700 | 0.3 |  |  | 72.5424
[29 empty] | 23 | 800 | 0.3 |  |  | 72.5424
[29 empty] | 24 | 900 | 0.3 |  |  | 72.5424
[29 empty] | 25 | 1000 | 0.3 |  |  | 72.5424
[29 empty] | 26 | 1200 | 0.3 |  |  | 72.5424
[29 empty] | 27 | 1500 | 0.3 |  |  | 72.5424
[29 empty] | 28 |  | 0.3 |  |  | 72.5424

## UGVDROP4 (hidden)
[17 empty] | Ampicity | Check
| Footage | Kw | Transformer | Trans Kw | [7 empty] | CONDUCTOR DATA DESIGN MANUAL |  |  |  |  | 1 PH | OK
Single PH | #REF! | #REF! | 15 | #REF! |  |  |  |  | Wire Ref | 1 | ALUMINUM CABLES OHMS / 1000 FT |  |  |  | Volt Drop | Amp Check | 3 PH | #N/A
Array | 0 | 0 | 15 | 0 |  |  |  |  | Volt Drop | 0 | SIZE | R | X | Z |  | 1 through 7 | 7 through 12
Three PH | 81 | 52 | 75 | 0 | [5 empty] | 1 | 2 | 0.267 | 0.0238 | 0.25067 | 0 | OK | NO
[10 empty] | 2 | 1/0 | 0.168 | 0.0241 | 0.1617 | 0 | OK | NO
[9 empty] | 1 | 3 | 3/0 | 0.105 | 0.0226 | 0.10435 | 0 | OK | NO
[9 empty] | 2 | 4 | 350 | 0.0505 | 0.0215 | 0.054822 | 0 | OK | NO
PF | ANGLE |  | 1-PH = 1 | SYSTEM |  | Cable Demand | KW |  | 3 | 5 | 500 | 0.0354 | 0.0207 | 0.040883 | 0 | OK | NO
0.9 | 25.8419 |  | 3-PH = 3 | 1 |  |  | 0 |  | 4 | 6 | 1000 | 0.0177 | 0.0199 | 0.024604 | 0 | OK | NO
VOLTAGE |  |  | RUN |  | FEET |  | L-AMPS |  |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C
120 | 240 |  | 1 |  | 0 |  | 0 |  |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | 600 Volt Secondary Aluminum Cable, DB Conduit (Direct Buried)
|  |  | IF 3 PH | [7 empty] | SIZE | R@65C | R@90C | X | Z | R@90C | Z |  | (With 7-1/2 Inches Centerline to Centerline Spacing Between Conduits)
|  |  | 4 | [7 empty] | 2 | 0.31061 | 0.33653 | 0.045 | 0.32249 | 0.2052 | 0.2043 |  | Cable Size | Conduit | Number of | Number of Runs
[11 empty] | 1 | 0.24432 | 0.26471 | 0.046 | 0.25829 | 0.1623 | 0.16612 |  | Size | Size | Conductors | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Single-Phase Transformers |  |  |  | Three-Phase Transformers | [6 empty] | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.2094 | 0.1334 | 0.13924 |  | 1000 | 5"DB | 3-1/C | 605 | 1104 | 1527 | 1892 | 2335 | 2526 | 2821 | 3080 | 3339 | 3550 | 3707 | 3828
[11 empty] | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.16944 | 0.1028 | 0.11126 |  | 500 | 4"DB | 3-1/C | 397 | 736 | 1029 | 1288 | 1595 | 1746 | 1953 | 2144 | 2313 | 2470 | 2607 | 2712
kVA |  | 15 |  | kVA |  | 75 |  |  |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.13724 | 0.0825 | 0.092557 |  | 350 | 3"DB | 2-1/C | 318 | 600 | 852 | 1076 | 1285 | 1482 | 1673 | 1840 | 2016 | 2160 | 2266 | 2376
Percentage Load |  | 0% |  | Percentage Load |  | N/A |  |  |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.11354 | 0.0653 | 0.076641 |  | 350 | 3"DB | 3-1/C | 313 | 586 | 822 | 1036 | 1230 | 1416 | 1589 | 1760 | 1908 | 2040 | 2145 | 2232
%Transformer Volt Drop |  | #N/A |  | %Transformer Volt Drop |  | 0 |  |  |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.098578 | 0.0552 | 0.067551 |  | 3/0 | 2"DB | 2-1/C | 202 | 386 | 552 | 704 | 875 | 984 | 1113 | 1232 | 1250 | 1440 | 1518 | 1608
Load on Transformer |  | 0 | KW |  |  | 0 | KW |  |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075795 | 0.0404 | 0.053796 |  | 3/0 | 3"DB | 3-1/C | 199 | 376 | 534 | 676 | 810 | 936 | 1057 | 1160 | 1269 | 1350 | 1419 | 1500
[11 empty] | 500 | 0.042235 | 0.04576 | 0.039 | 0.058184 | 0.0289 | 0.04301 |  | 1/0 | 2"DB | 2-1/C | 152 | 292 | 420 | 536 | 645 | 750 | 854 | 944 | 1044 | 1130 | 1188 | 1248
[11 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.043965 | 0.0199 | 0.034474 |  | #2 | 2"DB | 2-1/C | 113 | 218 | 315 | 404 | 490 | 570 | 651 | 720 | 792 | 860 | 913 | 960
[11 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.037873 | 0.0157 | 0.030258 |  | #8 | 1"DB | 1/C | 47 | 92 | 135 | 176 | 215 | 252 | 287 | 320 | 306 | 380 | 407 | 432
Ampacity OK |  | ALUMINUM CABLES |  |  |  | COPPER CABLES
Yes or No | Yes or No |  |  |  | TRANS. + CABLE |  |  | TRANS. + CABLE |  |  |  | 0.023 | 0.024115 |  | 0.077 | 0.080732
1-7 Runs | 8-12 Runs | SIZE | V - DROP | % DROP | %V-DROP | V - DROP | % DROP | V-DROP
OK | NO | 2 | 0 | 0 | #N/A | 0 | 0 | #N/A | [10 empty] | Single Phase Padmount Transformer Size
|  | 1 | 0 | 0 | #N/A | 0 | 0 | #N/A | [11 empty] | kVA
OK | NO | 1/0 | 0 | 0 | #N/A | 0 | 0 | #N/A | [10 empty] | Percentage | 15 | 25 | Number of Runs 1: 50; Number of Runs 2: 75; Number of Runs 3: 100; Number of Runs 4: 167; Number of Runs 5: Under 50% Loading
|  | 2/0 | 0 | 0 | #N/A | 0 | 0 | #N/A | [10 empty] | 50% | 1 | 1 | Number of Runs 1: 1; Number of Runs 2: 0.9; Number of Runs 3: 0.9; Number of Runs 4: 1; Number of Runs 6: #N/A
OK | NO | 3/0 | 0 | 0 | #N/A | 0 | 0 | #N/A | [10 empty] | 60% | 1.2 | 1.2 | Number of Runs 1: 1.2; Number of Runs 2: 1.1; Number of Runs 3: 1; Number of Runs 4: 1.2; Number of Runs 5: Over 50% Loading
|  | 4/0 | 0 | 0 | #N/A | 0 | 0 | #N/A | [10 empty] | 70% | 1.5 | 1.4 | Number of Runs 1: 1.4; Number of Runs 2: 1.3; Number of Runs 3: 1.2; Number of Runs 4: 1.4; Number of Runs 6: #N/A
|  | 250 | 0 | 0 | #N/A | 0 | 0 | #N/A | [8 empty] | 50 |  | 80% | 1.7 | 1.6 | Number of Runs 1: 1.6; Number of Runs 2: 1.5; Number of Runs 3: 1.4; Number of Runs 4: 1.6
OK | NO | 350 | 0 | 0 | #N/A | 0 | 0 | #N/A | [10 empty] | 90% | 1.9 | 1.8 | Number of Runs 1: 1.8; Number of Runs 2: 1.6; Number of Runs 3: 1.6; Number of Runs 4: 1.8
OK | NO | 500 | 0 | 0 | #N/A | 0 | 0 | #N/A | [8 empty] | #VALUE! |  | 100% | 2.1 | 2 | Number of Runs 1: 1.8; Number of Runs 2: 1.8; Number of Runs 3: 1.7; Number of Runs 4: 2
|  | 750 | 0 | 0 | #N/A | 0 | 0 | #N/A | [8 empty] | 60% |  | 110% | 2.3 | 2.2 | Number of Runs 1: 2; Number of Runs 2: 2; Number of Runs 3: 1.9; Number of Runs 4: 2.2
OK | NO | 1000 | 0 | 0 | #N/A | 0 | 0 | #N/A | [8 empty] | 0 |  | 120% | 2.5 | 2.4 | Number of Runs 1: 2.2; Number of Runs 2: 2.2; Number of Runs 3: 2.1; Number of Runs 4: 2.4
[17 empty] | 0 |  | 130% | 2.7 | 2.6 | Number of Runs 1: 2.4; Number of Runs 2: 2.4; Number of Runs 3: 2.3; Number of Runs 4: 2.6
[19 empty] | 140% | 2.9 | 2.8 | Number of Runs 1: 2.6; Number of Runs 2: 2.5; Number of Runs 3: 2.4; Number of Runs 4: 2.9
[17 empty] | 1.35 |  | 150% | 3.1 | 3 | Number of Runs 1: 2.8; Number of Runs 2: 2.7; Number of Runs 3: 2.6; Number of Runs 4: 3.1
[17 empty] | 1 |  | 160% | 3.3 | 3.2 | Number of Runs 1: 2.9; Number of Runs 2: 2.9; Number of Runs 3: 2.8; Number of Runs 4: 3.3
Number of Runs | [16 empty] | 50kVA |  | 170% | 3.5 | 3.4 | Number of Runs 1: 3; Number of Runs 2: 3.1; Number of Runs 3: 3.3; Number of Runs 4: 3.6
1 | [16 empty] | 70%
2 | [16 empty] | #N/A |  | 120/208V Three-Phase Padmount Transformer Size
3 | [18 empty] | Transformer | Kva
4 | [18 empty] | Loading | 45 | 75 | Number of Runs 1: 150; Number of Runs 2: 225; Number of Runs 3: 300; Number of Runs 4: 500; Number of Runs 5: 750; Number of Runs 6: 1000
5 | [18 empty] | 50% | 1.3 | 1.13 | Number of Runs 1: 0.89; Number of Runs 2: 0.91; Number of Runs 3: 0.98; Number of Runs 4: 1.54; Number of Runs 5: 2.03; Number of Runs 6: 1.9
6 | [18 empty] | 60% | 1.6 | 1.35 | Number of Runs 1: 1.07; Number of Runs 2: 1.1; Number of Runs 3: 1.17; Number of Runs 4: 1.8; Number of Runs 5: 2.43; Number of Runs 6: 2.33
7 | [18 empty] | 70% | 1.8 | 1.58 | Number of Runs 1: 1.2; Number of Runs 2: 1.3; Number of Runs 3: 1.37; Number of Runs 4: 2.1; Number of Runs 5: 2.84; Number of Runs 6: 2.72
8 | [18 empty] | 80% | 2.1 | 1.81 | Number of Runs 1: 1.43; Number of Runs 2: 1.46; Number of Runs 3: 1.56; Number of Runs 4: 2.4; Number of Runs 5: 3.2; Number of Runs 6: 3
9 | [18 empty] | 90% | 2.4 | 2.03 | Number of Runs 1: 1.6; Number of Runs 2: 1.64; Number of Runs 3: 1.76; Number of Runs 4: 2.7; Number of Runs 5: 3.6; Number of Runs 6: 3.4
10 | [18 empty] | 100% | 2.6 | 2.26 | Number of Runs 1: 1.78; Number of Runs 2: 1.83; Number of Runs 3: 1.9; Number of Runs 4: 3; Number of Runs 5: 4; Number of Runs 6: 3.8
11 | [18 empty] | 110% | 2.9 | 2.48 | Number of Runs 1: 1.96; Number of Runs 2: 2.01; Number of Runs 3: 2.1; Number of Runs 4: 3.3; Number of Runs 5: 4.3; Number of Runs 6: 4.2
12 | [18 empty] | 120% | 3.2 | 2.71 | Number of Runs 1: 2.14; Number of Runs 2: 2.2; Number of Runs 3: 2.3; Number of Runs 4: 3.6; Number of Runs 5: 4.7; Number of Runs 6: 4.6
[19 empty] | 130% | 3.4 | 2.94 | Number of Runs 1: 2.39; Number of Runs 2: 2.49; Number of Runs 3: 2.72; Number of Runs 4: 4; Number of Runs 5: 5.4; Number of Runs 6: 5.2
[19 empty] | 140% | 3.7 | 3.16 | Number of Runs 1: 2.57; Number of Runs 2: 2.68; Number of Runs 3: 2.93; Number of Runs 4: 4.44; Number of Runs 5: 5.9; Number of Runs 6: 5.6
[19 empty] | 150% | 4 | 3.69 | Number of Runs 1: 2.91; Number of Runs 2: 3.07; Number of Runs 3: 3.37; Number of Runs 4: 5; Number of Runs 5: 6.8; Number of Runs 6: 6.5; Number of Runs 7: Under 50% Loading
#N/A
Over 50% Loading
[19 empty] | 277/480V Three-Phase Padmount Transformer Size |  |  | Number of Runs 8: 0
[19 empty] | Transformer | Kva
[19 empty] | Loading | 75 | 150 | 225 | 300 | 500 | 750 | 1000 | 1500 | 2000 | 2500 | 3000
[19 empty] | 50% | 1.07 | 0.92 | 0.72 | 0.96 | 0.93 | 1.93 | 1.9 | 1.9 | 1.8 | 1.8 | 1.9
[19 empty] | 60% | 1.29 | 1.1 | 0.87 | 1.15 | 1.12 | 2.32 | 2.34 | 2.34 | 2.2 | 2.2 | 2.2
[19 empty] | 70% | 1.5 | 1.3 | 1.01 | 1.3 | 1.3 | 2.6 | 2.73 | 2.6 | 2.63 | 2.6 | 2.6
[19 empty] | 80% | 1.72 | 1.47 | 1.16 | 1.54 | 1.49 | 3 | 3 | 3 | 2.9 | 3.04 | 3
[19 empty] | 90% | 1.93 | 1.65 | 1.3 | 1.73 | 1.68 | 3.4 | 3.4 | 3.4 | 3.3 | 3.3 | 3.3
[19 empty] | 100% | 2.1 | 1.84 | 1.4 | 1.92 | 1.86 | 3.8 | 3.8 | 3.8 | 3.7 | 3.7 | 3.7
[19 empty] | 110% | 2.36 | 2.02 | 1.59 | 2.11 | 2 | 4.1 | 4.2 | 4.2 | 4 | 4.1 | 4.1
[19 empty] | 120% | 2.58 | 2.21 | 1.73 | 2.31 | 2.24 | 4.5 | 4.6 | 4.5 | 4.4 | 4.4 | 4.4
[19 empty] | 130% | 2.79 | 2.5 | 1.88 | 2.6 | 2.5 | 5.2 | 5.2 | 5.3 | 5.1 | 5.2 | 5.2
[19 empty] | 140% | 3.01 | 2.6 | 2.1 | 2.8 | 2.7 | 5.6 | 5.6 | 5.7 | 5.5 | 5.6 | 5.7
[19 empty] | 150% | 3.5 | 3 | 2.4 | 3.3 | 3.1 | 6.4 | 65 | 6.5 | 6.3 | 6.4 | 6.5
2

## UGFLCKER4 (hidden)
[34 empty] | 15 | 2.1 | 1.7 | 1.2 | updated 17th Feb. 2000 with table 5 of 5413.7
[34 empty] | 25 | 2 | 1.6 | 1.2
[34 empty] | 50 | 2.1 | 1.3 | 1.7
[34 empty] | 75 | 2 | 1.1 | 1.8 | 1.051 | 1.751
[34 empty] | 100 | 2.2 | 1.1 | 1.9
[17 empty] | LRC VALUES (updated 5 FEB 1998) | [15 empty] | Single Phase kVA | 167 | 2.3 | 1.1 | 2
[18 empty] | SINGLE-PHASE MOTOR SIZES IN HP | [15 empty] | 45 | 2.7153 | 1.91 | 1.93
[17 empty] | VOLTAGE | 1 | 1.5 | 2 | [13 empty] | 75 | 2.2888 | 1.72 | 1.51 | 1.62 | 1.46
[17 empty] | 120 | 46 | 69 | 92 | [13 empty] | 150 | 1.916 | 1.14 | 1.54
[34 empty] | 225 | 1.9462 | 1.19 | 1.54
[11 empty] | CONDUCTOR DATA DESIGN MANUAL | [22 empty] | 300 | 2.2897 | 1.02 | 2.05
PF |  | ANGLE | 1-PH = 1 | # OF PHASES | HP | 1Ph-LRC | 1Ph-XKMR% |  |  | ALUMINUM CABLES OHMS / 1000 FT | [23 empty] | 500 | 4.5034 | 0.81 | 4.43
0.75 |  | 41.4096 | 3-PH = 3 | 1 | 4.5 | 103 | 3.4093 | 1.7 | 1-Ph | SIZE | R | X | Z | L-AMPS |  |  | LRC VALUES (updated 5 FEB 1998) | [16 empty] | 750 | 6.0451 | 0.95 | 5.97
[6 empty] | 3Ph-LRC |  | #N/A | 3-Ph | 2 | 0.267 | 0.0238 | 0.21599 | 103 |  |  |  | SINGLE-PHASE MOTOR SIZES IN HORSE POWER | [15 empty] | 1000 | 5.82 | 0.9 | 5.75
[6 empty] | n/a |  | X |  | 1/0 | 0.168 | 0.0241 | 0.14194 |  |  |  | VOLTAGE | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 10 | [7 empty] | 1500 | 0 | 0 | 0
VOLTAGE |  |  | RUN | FEET | KW | XFMR KVA | 3Ph-XFMR % | 1.2 | 1-Ph | 3/0 | 0.105 | 0.0226 | 0.093698 |  |  |  | 240 | 27 | 34 | 46 | 69 | 103 | 115 | 140 | 175 | 218 | [7 empty] | 2000 | 0 | 0 | 0
120 |  | 240 | 1 | 0 | 18.54 | 15 | 0 | #N/A |  | 350 | 0.0505 | 0.0215 | 0.052096 | [20 empty] | 2500 | 0 | 0 | 0
[10 empty] | 500 | 0.0354 | 0.0207 | 0.040242 | [20 empty] | 3000 | 0 | 0 | 0
ALUMINUM CABLES |  |  |  |  | COPPER CABLES | [27 empty] | Three Phase kVA | Three Phase kVA | Z% | R% | X%
|  | CABLE | CABLE | *TOTAL% | CABLE | CABLE | *TOTAL% |  |  | 1000 | 0.0177 | 0.0199 | 0.026438 | [20 empty] | updated 17th Feb. 2000 with table 9 of 5413.7
SIZE |  | (VOLTS) | ( % ) | FLICKER | (VOLTS) | ( % ) | FLICKER |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C | [6 empty] | LRC VALUES (updated 31dec1997)
2 |  | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | MOTOR SIZES IN HORSE POWER
1 |  | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | SIZE | R@65C | R@90C | X | Z | R@90C | Z | VOLTAGE | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200
1/0 |  | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 2 | 0.31061 | 0.33653 | 0.045 | 0.28216 | 0.2052 | 0.18366 | 208 | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
2/0 |  | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 1 | 0.24432 | 0.26471 | 0.046 | 0.22896 | 0.1623 | 0.15215 | 240 | 64 | 85 | 92 | 106 | 127 | 162 | 232 | 290 | 365 | 435 | 580 | 725 | 1085 | 1450 | 2170
3/0 |  | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.18762 | 0.1334 | 0.12915 | 480 | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
4/0 |  | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.15403 | 0.1028 | 0.10554
250 |  | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.12689 | 0.0825 | 0.089655
350 |  | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.10684 | 0.0653 | 0.076094
500 |  | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.094374 | 0.0552 | 0.068519
750 |  | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075091 | 0.0404 | 0.056758 |  | 3 Phase | Three-Phase Motor (Sized in HP) | [15 empty] | Transformer Data |  | X/R
1000 |  | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 500 | 0.042235 | 0.04576 | 0.039 | 0.060116 | 0.0289 | 0.047471 |  | Trans | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200 | R | X | Ratio | Z%
[10 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.047969 | 0.0199 | 0.04006 |  | 45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.0191 | 0.0193 | 1.0105 | 2.715%
[10 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.042594 | 0.0157 | 0.036248 |  | 75 | 0.66522 | 0.88072 | 0.95567 | 1.0962 | 1.3117 | 1.6771 | 2.4079 | 3.0076 | 3.7852 | 4.5066 | 6.0057 | 7.5142 | 11.2432 | 15.019 | 22.4864 | 30.0474 | 0.0172 | 0.0151 | 0.87791 | 2.289%
WITH REDUCED LRC TO 770A OR 50HP |  |  |  |  | *TOTAL FLICKER = CABLE (%) + XMFR (%) | [12 empty] | 150 | 0.3078 | 0.40751 | 0.44219 | 0.54094 | 0.60693 | 0.776 | 1.1141 | 1.3916 | 1.7514 | 2.0852 | 2.7789 | 3.4768 | 5.2022 | 6.9493 | 10.4045 | 13.903 | 0.0114 | 0.0154 | 1.3509 | 1.916%
[11 empty] | 0.023 | 0.024115 |  | 0.077 | 0.080732 |  |  | 225 | 0.20691 | 0.27393 | 0.29724 | 0.34096 | 0.40798 | 0.52163 | 0.74894 | 0.93544 | 1.1773 | 1.4017 | 1.868 | 2.3372 | 3.497 | 4.6714 | 6.994 | 9.3457 | 0.0119 | 0.0154 | 1.2941 | 1.946%
[18 empty] | 300 | 0.19214 | 0.25438 | 0.27603 | 0.31663 | 0.37887 | 0.48441 | 0.69549 | 0.86869 | 1.0933 | 1.3017 | 1.7347 | 2.1704 | 3.2474 | 4.338 | 6.4949 | 8.6788 | 0.0102 | 0.0205 | 2.0098 | 2.29%
Lookup Value |  |  | 0 | [14 empty] | 500 | 0.22773 | 0.3015 | 0.32716 | 0.37527 | 0.44904 | 0.57413 | 0.82432 | 1.0296 | 1.2958 | 1.5428 | 2.056 | 2.5724 | 3.8489 | 5.1415 | 7.6979 | 10.2863 | 0.0081 | 0.0443 | 5.4691 | 4.503%
Lookup |  | Wire | Volatge Drop | % Volatge Drop | [13 empty] | 750 | 0.20315 | 0.26896 | 0.29185 | 0.33476 | 0.40057 | 0.51216 | 0.73534 | 0.91846 | 1.1559 | 1.3763 | 1.8341 | 2.2947 | 3.4335 | 4.5866 | 6.867 | 9.176 | 0.0095 | 0.0597 | 6.2842 | 6.045%
1 |  | 2 | 0 | 0 | [13 empty] | 1000 | 0.14663 | 0.19413 | 0.21065 | 0.24163 | 0.28913 | 0.36968 | 0.53076 | 0.66294 | 0.83435 | 0.99337 | 1.3238 | 1.6563 | 2.4783 | 3.3106 | 4.9565 | 6.6232 | 0.009 | 0.0575 | 6.3889 | 5.82%
2 |  | 1/0 | 0 | 0 | [13 empty] | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
3 | 1 | 3/0 | 0 | 0 | [13 empty] | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
4 | 2 | 350 | 0 | 0 | [13 empty] | 2500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
5 | 3 | 500 | 0 | 0 | [13 empty] | 3000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
6 | 4 | 1000 | 0 | 0 | [13 empty] | Locked Rotor Current
[18 empty] | @208V | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
[18 empty] | @480V | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
1 Phase
Trans
(kVA)
25
50
75
100
[18 empty] | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE |  |  | Three Phase Motor Data |  | Three PH Motor REF | 9 | HP | #N/A
[18 empty] | 1 | 1 |  |  | 1HP | 0.75 | 41.4096 |  |  | LOOKUP | HP | P.F. | REF
[18 empty] | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096 |  |  | 1 | 3 | 0.3 | 11 | SER 1 | 72.5424
[18 empty] | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096 |  |  | 2 | 4.5 | 0.3 | 14 | SER 2 | 72.5424
[18 empty] | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096 |  |  | 3 | 5 | 0.3 | 9 | SER 3 | 72.5424
[18 empty] | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096 |  |  | 4 | 6 | 0.3 |  | SEC 1 | 72.5424
[18 empty] | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096 |  |  | 5 | 7.5 | 0.3 |  |  | 72.5424
[18 empty] | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096 |  |  | 6 | 10 | 0.3 |  |  | 72.5424
[18 empty] | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096 |  |  | 7 | 15 | 0.3 |  |  | 72.5424
[18 empty] | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096 |  |  | 8 | 20 | 0.3 |  |  | 72.5424
[18 empty] | SINGLE PHASE LOOKUPS |  | Single PH Motor REF |  | 5 | HP | #N/A |  |  | 9 | 25 | 0.3 |  |  | 72.5424
[27 empty] | 10 | 30 | 0.3 |  |  | 72.5424
[27 empty] | 11 | 40 | 0.3 |  |  | 72.5424
[27 empty] | 12 | 50 | 0.3 |  |  | 72.5424
[27 empty] | 13 | 60 | 0.3 |  |  | 72.5424
[27 empty] | 14 | 75 | 0.3 |  |  | 72.5424
[27 empty] | 15 | 100 | 0.3 |  |  | 72.5424
[27 empty] | 16 | 150 | 0.3 |  |  | 72.5424
[27 empty] | 17 | 200 | 0.3 |  |  | 72.5424
[27 empty] | 18 | 250 | 0.3 |  |  | 72.5424
[27 empty] | 19 | 300 | 0.3 |  |  | 72.5424
[27 empty] | 20 | 400 | 0.3 |  |  | 72.5424
[27 empty] | 21 | 500 | 0.3 |  |  | 72.5424
[27 empty] | 22 | 600 | 0.3 |  |  | 72.5424
[27 empty] | 23 | 700 | 0.3 |  |  | 72.5424
[27 empty] | 24 | 800 | 0.3 |  |  | 72.5424
[27 empty] | 25 | 900 | 0.3 |  |  | 72.5424
[27 empty] | 26 | 1000 | 0.3 |  |  | 72.5424
[27 empty] | 27 | 1200 | 0.3 |  |  | 72.5424
[27 empty] | 28 | 1500 | 0.3 |  |  | 72.5424

## UGVDROP5 (hidden)
[17 empty] | Ampicity | Check
Transformer | Trans Kw | [10 empty] | CONDUCTOR DATA DESIGN MANUAL |  |  |  |  | 1 PH | OK
15 | #REF! | [7 empty] | Wire Ref | 1 | ALUMINUM CABLES OHMS / 1000 FT |  |  |  | Volt Drop | Amp Check | 3 PH | #N/A
15 | 0 | [7 empty] | Volt Drop | 0 | SIZE | R | X | Z |  | 1 through 7 | 7 through 12
75 | 0 | [8 empty] | 1 | 2 | 0.267 | 0.0238 | 0.25067 | 0 | OK | NO
[10 empty] | 2 | 1/0 | 0.168 | 0.0241 | 0.1617 | 0 | OK | NO
[9 empty] | 1 | 3 | 3/0 | 0.105 | 0.0226 | 0.10435 | 0 | OK | NO
[9 empty] | 2 | 4 | 350 | 0.0505 | 0.0215 | 0.054822 | 0 | OK | NO
PF | ANGLE |  | 1-PH = 1 | SYSTEM |  | Cable Demand | KW |  | 3 | 5 | 500 | 0.0354 | 0.0207 | 0.040883 | 0 | OK | NO
0.9 | 25.8419 |  | 3-PH = 3 | 1 |  |  | 0 |  | 4 | 6 | 1000 | 0.0177 | 0.0199 | 0.024604 | 0 | OK | NO
VOLTAGE |  |  | RUN |  | FEET |  | L-AMPS |  |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C
120 | 240 |  | 1 |  | 0 |  | 0 |  |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | 600 Volt Secondary Aluminum Cable, DB Conduit (Direct Buried)
|  |  | IF 3 PH | [7 empty] | SIZE | R@65C | R@90C | X | Z | R@90C | Z |  | (With 7-1/2 Inches Centerline to Centerline Spacing Between Conduits)
|  |  | 1 | [7 empty] | 2 | 0.31061 | 0.33653 | 0.045 | 0.32249 | 0.2052 | 0.2043 |  | Cable Size | Conduit | Number of | Number of Runs
[11 empty] | 1 | 0.24432 | 0.26471 | 0.046 | 0.25829 | 0.1623 | 0.16612 |  | Size | Size | Conductors | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Single-Phase Transformers |  |  |  | Three-Phase Transformers | [6 empty] | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.2094 | 0.1334 | 0.13924 |  | 1000 | 5"DB | 3-1/C | 605 | 1104 | 1527 | 1892 | 2335 | 2526 | 2821 | 3080 | 3339 | 3550 | 3707 | 3828
[11 empty] | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.16944 | 0.1028 | 0.11126 |  | 500 | 4"DB | 3-1/C | 397 | 736 | 1029 | 1288 | 1595 | 1746 | 1953 | 2144 | 2313 | 2470 | 2607 | 2712
kVA |  | 15 |  | kVA |  | 75 |  |  |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.13724 | 0.0825 | 0.092557 |  | 350 | 3"DB | 2-1/C | 318 | 600 | 852 | 1076 | 1285 | 1482 | 1673 | 1840 | 2016 | 2160 | 2266 | 2376
Percentage Load |  | 111.1% |  | Percentage Load |  | N/A |  |  |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.11354 | 0.0653 | 0.076641 |  | 350 | 3"DB | 3-1/C | 313 | 586 | 822 | 1036 | 1230 | 1416 | 1589 | 1760 | 1908 | 2040 | 2145 | 2232
%Transformer Volt Drop |  | 2.3 |  | %Transformer Volt Drop |  | 0 |  |  |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.098578 | 0.0552 | 0.067551 |  | 3/0 | 2"DB | 2-1/C | 202 | 386 | 552 | 704 | 875 | 984 | 1113 | 1232 | 1250 | 1440 | 1518 | 1608
Load on Transformer |  | 15 | KW |  |  | 0 | KW |  |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075795 | 0.0404 | 0.053796 |  | 3/0 | 3"DB | 3-1/C | 199 | 376 | 534 | 676 | 810 | 936 | 1057 | 1160 | 1269 | 1350 | 1419 | 1500
[11 empty] | 500 | 0.042235 | 0.04576 | 0.039 | 0.058184 | 0.0289 | 0.04301 |  | 1/0 | 2"DB | 2-1/C | 152 | 292 | 420 | 536 | 645 | 750 | 854 | 944 | 1044 | 1130 | 1188 | 1248
[11 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.043965 | 0.0199 | 0.034474 |  | #2 | 2"DB | 2-1/C | 113 | 218 | 315 | 404 | 490 | 570 | 651 | 720 | 792 | 860 | 913 | 960
[11 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.037873 | 0.0157 | 0.030258 |  | #8 | 1"DB | 1/C | 47 | 92 | 135 | 176 | 215 | 252 | 287 | 320 | 306 | 380 | 407 | 432
Ampacity OK |  | ALUMINUM CABLES |  |  |  | COPPER CABLES
Yes or No | Yes or No |  |  |  | TRANS. + CABLE |  |  | TRANS. + CABLE |  |  |  | 0.023 | 0.024115 |  | 0.077 | 0.080732
1-7 Runs | 8-12 Runs | SIZE | V - DROP | % DROP | %V-DROP | V - DROP | % DROP | V-DROP
OK | NO | 2 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Single Phase Padmount Transformer Size
|  | 1 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [11 empty] | kVA
OK | NO | 1/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Percentage | 15 | 25 | Number of Runs 1: 50; Number of Runs 2: 75; Number of Runs 3: 100; Number of Runs 4: 167; Number of Runs 5: Under 50% Loading
|  | 2/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 50% | 1 | 1 | Number of Runs 1: 1; Number of Runs 2: 0.9; Number of Runs 3: 0.9; Number of Runs 4: 1; Number of Runs 6: #N/A
OK | NO | 3/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 60% | 1.2 | 1.2 | Number of Runs 1: 1.2; Number of Runs 2: 1.1; Number of Runs 3: 1; Number of Runs 4: 1.2; Number of Runs 5: Over 50% Loading
|  | 4/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 70% | 1.5 | 1.4 | Number of Runs 1: 1.4; Number of Runs 2: 1.3; Number of Runs 3: 1.2; Number of Runs 4: 1.4; Number of Runs 6: 2.3
|  | 250 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 50 |  | 80% | 1.7 | 1.6 | Number of Runs 1: 1.6; Number of Runs 2: 1.5; Number of Runs 3: 1.4; Number of Runs 4: 1.6
OK | NO | 350 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 90% | 1.9 | 1.8 | Number of Runs 1: 1.8; Number of Runs 2: 1.6; Number of Runs 3: 1.6; Number of Runs 4: 1.8
OK | NO | 500 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | #VALUE! |  | 100% | 2.1 | 2 | Number of Runs 1: 1.8; Number of Runs 2: 1.8; Number of Runs 3: 1.7; Number of Runs 4: 2
|  | 750 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 60% |  | 110% | 2.3 | 2.2 | Number of Runs 1: 2; Number of Runs 2: 2; Number of Runs 3: 1.9; Number of Runs 4: 2.2
OK | NO | 1000 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 0 |  | 120% | 2.5 | 2.4 | Number of Runs 1: 2.2; Number of Runs 2: 2.2; Number of Runs 3: 2.1; Number of Runs 4: 2.4
[17 empty] | 0 |  | 130% | 2.7 | 2.6 | Number of Runs 1: 2.4; Number of Runs 2: 2.4; Number of Runs 3: 2.3; Number of Runs 4: 2.6
[19 empty] | 140% | 2.9 | 2.8 | Number of Runs 1: 2.6; Number of Runs 2: 2.5; Number of Runs 3: 2.4; Number of Runs 4: 2.9
[17 empty] | 1.35 |  | 150% | 3.1 | 3 | Number of Runs 1: 2.8; Number of Runs 2: 2.7; Number of Runs 3: 2.6; Number of Runs 4: 3.1
[17 empty] | 1 |  | 160% | 3.3 | 3.2 | Number of Runs 1: 2.9; Number of Runs 2: 2.9; Number of Runs 3: 2.8; Number of Runs 4: 3.3
Number of Runs | [16 empty] | 50kVA |  | 170% | 3.5 | 3.4 | Number of Runs 1: 3; Number of Runs 2: 3.1; Number of Runs 3: 3.3; Number of Runs 4: 3.6
1 | [16 empty] | 70%
2 | [16 empty] | #N/A |  | 120/208V Three-Phase Padmount Transformer Size
3 | [18 empty] | Transformer | Kva
4 | [18 empty] | Loading | 45 | 75 | Number of Runs 1: 150; Number of Runs 2: 225; Number of Runs 3: 300; Number of Runs 4: 500; Number of Runs 5: 750; Number of Runs 6: 1000
5 | [18 empty] | 50% | 1.3 | 1.13 | Number of Runs 1: 0.89; Number of Runs 2: 0.91; Number of Runs 3: 0.98; Number of Runs 4: 1.54; Number of Runs 5: 2.03; Number of Runs 6: 1.9
6 | [18 empty] | 60% | 1.6 | 1.35 | Number of Runs 1: 1.07; Number of Runs 2: 1.1; Number of Runs 3: 1.17; Number of Runs 4: 1.8; Number of Runs 5: 2.43; Number of Runs 6: 2.33
7 | [18 empty] | 70% | 1.8 | 1.58 | Number of Runs 1: 1.2; Number of Runs 2: 1.3; Number of Runs 3: 1.37; Number of Runs 4: 2.1; Number of Runs 5: 2.84; Number of Runs 6: 2.72
8 | [18 empty] | 80% | 2.1 | 1.81 | Number of Runs 1: 1.43; Number of Runs 2: 1.46; Number of Runs 3: 1.56; Number of Runs 4: 2.4; Number of Runs 5: 3.2; Number of Runs 6: 3
9 | [18 empty] | 90% | 2.4 | 2.03 | Number of Runs 1: 1.6; Number of Runs 2: 1.64; Number of Runs 3: 1.76; Number of Runs 4: 2.7; Number of Runs 5: 3.6; Number of Runs 6: 3.4
10 | [18 empty] | 100% | 2.6 | 2.26 | Number of Runs 1: 1.78; Number of Runs 2: 1.83; Number of Runs 3: 1.9; Number of Runs 4: 3; Number of Runs 5: 4; Number of Runs 6: 3.8
11 | [18 empty] | 110% | 2.9 | 2.48 | Number of Runs 1: 1.96; Number of Runs 2: 2.01; Number of Runs 3: 2.1; Number of Runs 4: 3.3; Number of Runs 5: 4.3; Number of Runs 6: 4.2
12 | [18 empty] | 120% | 3.2 | 2.71 | Number of Runs 1: 2.14; Number of Runs 2: 2.2; Number of Runs 3: 2.3; Number of Runs 4: 3.6; Number of Runs 5: 4.7; Number of Runs 6: 4.6
[19 empty] | 130% | 3.4 | 2.94 | Number of Runs 1: 2.39; Number of Runs 2: 2.49; Number of Runs 3: 2.72; Number of Runs 4: 4; Number of Runs 5: 5.4; Number of Runs 6: 5.2
[19 empty] | 140% | 3.7 | 3.16 | Number of Runs 1: 2.57; Number of Runs 2: 2.68; Number of Runs 3: 2.93; Number of Runs 4: 4.44; Number of Runs 5: 5.9; Number of Runs 6: 5.6
[19 empty] | 150% | 4 | 3.69 | Number of Runs 1: 2.91; Number of Runs 2: 3.07; Number of Runs 3: 3.37; Number of Runs 4: 5; Number of Runs 5: 6.8; Number of Runs 6: 6.5; Number of Runs 7: Under 50% Loading
#N/A
Over 50% Loading
[19 empty] | 277/480V Three-Phase Padmount Transformer Size |  |  | Number of Runs 8: 0
[19 empty] | Transformer | Kva
[19 empty] | Loading | 75 | 150 | 225 | 300 | 500 | 750 | 1000 | 1500 | 2000 | 2500 | 3000
[19 empty] | 50% | 1.07 | 0.92 | 0.72 | 0.96 | 0.93 | 1.93 | 1.9 | 1.9 | 1.8 | 1.8 | 1.9
[19 empty] | 60% | 1.29 | 1.1 | 0.87 | 1.15 | 1.12 | 2.32 | 2.34 | 2.34 | 2.2 | 2.2 | 2.2
[19 empty] | 70% | 1.5 | 1.3 | 1.01 | 1.3 | 1.3 | 2.6 | 2.73 | 2.6 | 2.63 | 2.6 | 2.6
[19 empty] | 80% | 1.72 | 1.47 | 1.16 | 1.54 | 1.49 | 3 | 3 | 3 | 2.9 | 3.04 | 3
[19 empty] | 90% | 1.93 | 1.65 | 1.3 | 1.73 | 1.68 | 3.4 | 3.4 | 3.4 | 3.3 | 3.3 | 3.3
[19 empty] | 100% | 2.1 | 1.84 | 1.4 | 1.92 | 1.86 | 3.8 | 3.8 | 3.8 | 3.7 | 3.7 | 3.7
[19 empty] | 110% | 2.36 | 2.02 | 1.59 | 2.11 | 2 | 4.1 | 4.2 | 4.2 | 4 | 4.1 | 4.1
[19 empty] | 120% | 2.58 | 2.21 | 1.73 | 2.31 | 2.24 | 4.5 | 4.6 | 4.5 | 4.4 | 4.4 | 4.4
[19 empty] | 130% | 2.79 | 2.5 | 1.88 | 2.6 | 2.5 | 5.2 | 5.2 | 5.3 | 5.1 | 5.2 | 5.2
[19 empty] | 140% | 3.01 | 2.6 | 2.1 | 2.8 | 2.7 | 5.6 | 5.6 | 5.7 | 5.5 | 5.6 | 5.7
[19 empty] | 150% | 3.5 | 3 | 2.4 | 3.3 | 3.1 | 6.4 | 65 | 6.5 | 6.3 | 6.4 | 6.5
2

## UGFLCKER5 (hidden)
[33 empty] | 15 | 2.1 | 1.7 | 1.2 | updated 17th Feb. 2000 with table 5 of 5413.7
[33 empty] | 25 | 2 | 1.6 | 1.2
[33 empty] | 50 | 2.1 | 1.3 | 1.7
[33 empty] | 75 | 2 | 1.1 | 1.8 | 1.051 | 1.751
[33 empty] | 100 | 2.2 | 1.1 | 1.9
[16 empty] | LRC VALUES (updated 5 FEB 1998) | [15 empty] | Single Phase kVA | 167 | 2.3 | 1.1 | 2
[17 empty] | SINGLE-PHASE MOTOR SIZES IN HP | [15 empty] | 45 | 2.7153 | 1.91 | 1.93
[16 empty] | VOLTAGE | 1 | 1.5 | 2 | [13 empty] | 75 | 2.2888 | 1.72 | 1.51 | 1.62 | 1.46
[16 empty] | 120 | 46 | 69 | 92 | [13 empty] | 150 | 1.916 | 1.14 | 1.54
[33 empty] | 225 | 1.9462 | 1.19 | 1.54
[10 empty] | CONDUCTOR DATA DESIGN MANUAL | [22 empty] | 300 | 2.2897 | 1.02 | 2.05
PF | ANGLE | 1-PH = 1 | # OF PHASES | HP | 1Ph-LRC | 1Ph-XKMR% |  |  | ALUMINUM CABLES OHMS / 1000 FT | [23 empty] | 500 | 4.5034 | 0.81 | 4.43
0.75 | 41.4096 | 3-PH = 3 | 1 | 4.5 | 103 | 3.4093 | 1.7 | 1-Ph | SIZE | R | X | Z | L-AMPS |  |  | LRC VALUES (updated 5 FEB 1998) | [16 empty] | 750 | 6.0451 | 0.95 | 5.97
[5 empty] | 3Ph-LRC |  | #N/A | 3-Ph | 2 | 0.267 | 0.0238 | 0.21599 | 103 |  |  |  | SINGLE-PHASE MOTOR SIZES IN HORSE POWER | [15 empty] | 1000 | 5.82 | 0.9 | 5.75
[5 empty] | n/a |  | X |  | 1/0 | 0.168 | 0.0241 | 0.14194 |  |  |  | VOLTAGE | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 10 | [7 empty] | 1500 | 0 | 0 | 0
VOLTAGE |  | RUN | FEET | KW | XFMR KVA | 3Ph-XFMR % | 1.2 | 1-Ph | 3/0 | 0.105 | 0.0226 | 0.093698 |  |  |  | 240 | 27 | 34 | 46 | 69 | 103 | 115 | 140 | 175 | 218 | [7 empty] | 2000 | 0 | 0 | 0
120 | 240 | 1 | 0 | 18.54 | 15 | 0 | #N/A |  | 350 | 0.0505 | 0.0215 | 0.052096 | [20 empty] | 2500 | 0 | 0 | 0
[9 empty] | 500 | 0.0354 | 0.0207 | 0.040242 | [20 empty] | 3000 | 0 | 0 | 0
ALUMINUM CABLES |  |  |  | COPPER CABLES | [27 empty] | Three Phase kVA | Three Phase kVA | Z% | R% | X%
| CABLE | CABLE | *TOTAL% | CABLE | CABLE | *TOTAL% |  |  | 1000 | 0.0177 | 0.0199 | 0.026438 | [20 empty] | updated 17th Feb. 2000 with table 9 of 5413.7
SIZE | (VOLTS) | ( % ) | FLICKER | (VOLTS) | ( % ) | FLICKER |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C | [6 empty] | LRC VALUES (updated 31dec1997)
2 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | MOTOR SIZES IN HORSE POWER
1 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | SIZE | R@65C | R@90C | X | Z | R@90C | Z | VOLTAGE | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200
1/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 2 | 0.31061 | 0.33653 | 0.045 | 0.28216 | 0.2052 | 0.18366 | 208 | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
2/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 1 | 0.24432 | 0.26471 | 0.046 | 0.22896 | 0.1623 | 0.15215 | 240 | 64 | 85 | 92 | 106 | 127 | 162 | 232 | 290 | 365 | 435 | 580 | 725 | 1085 | 1450 | 2170
3/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.18762 | 0.1334 | 0.12915 | 480 | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
4/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.15403 | 0.1028 | 0.10554
250 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.12689 | 0.0825 | 0.089655
350 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.10684 | 0.0653 | 0.076094
500 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.094374 | 0.0552 | 0.068519
750 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075091 | 0.0404 | 0.056758 |  | 3 Phase | Three-Phase Motor (Sized in HP) | [15 empty] | Transformer Data |  | X/R
1000 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 500 | 0.042235 | 0.04576 | 0.039 | 0.060116 | 0.0289 | 0.047471 |  | Trans | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200 | R | X | Ratio | Z%
[9 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.047969 | 0.0199 | 0.04006 |  | 45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.0191 | 0.0193 | 1.0105 | 2.715%
[9 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.042594 | 0.0157 | 0.036248 |  | 75 | 0.66522 | 0.88072 | 0.95567 | 1.0962 | 1.3117 | 1.6771 | 2.4079 | 3.0076 | 3.7852 | 4.5066 | 6.0057 | 7.5142 | 11.2432 | 15.019 | 22.4864 | 30.0474 | 0.0172 | 0.0151 | 0.87791 | 2.289%
WITH REDUCED LRC TO 770A OR 50HP |  |  |  | *TOTAL FLICKER = CABLE (%) + XMFR (%) | [12 empty] | 150 | 0.3078 | 0.40751 | 0.44219 | 0.54094 | 0.60693 | 0.776 | 1.1141 | 1.3916 | 1.7514 | 2.0852 | 2.7789 | 3.4768 | 5.2022 | 6.9493 | 10.4045 | 13.903 | 0.0114 | 0.0154 | 1.3509 | 1.916%
[10 empty] | 0.023 | 0.024115 |  | 0.077 | 0.080732 |  |  | 225 | 0.20691 | 0.27393 | 0.29724 | 0.34096 | 0.40798 | 0.52163 | 0.74894 | 0.93544 | 1.1773 | 1.4017 | 1.868 | 2.3372 | 3.497 | 4.6714 | 6.994 | 9.3457 | 0.0119 | 0.0154 | 1.2941 | 1.946%
[17 empty] | 300 | 0.19214 | 0.25438 | 0.27603 | 0.31663 | 0.37887 | 0.48441 | 0.69549 | 0.86869 | 1.0933 | 1.3017 | 1.7347 | 2.1704 | 3.2474 | 4.338 | 6.4949 | 8.6788 | 0.0102 | 0.0205 | 2.0098 | 2.29%
Lookup Value |  | 0 | [14 empty] | 500 | 0.22773 | 0.3015 | 0.32716 | 0.37527 | 0.44904 | 0.57413 | 0.82432 | 1.0296 | 1.2958 | 1.5428 | 2.056 | 2.5724 | 3.8489 | 5.1415 | 7.6979 | 10.2863 | 0.0081 | 0.0443 | 5.4691 | 4.503%
Lookup | Wire | Volatge Drop | % Volatge Drop | [13 empty] | 750 | 0.20315 | 0.26896 | 0.29185 | 0.33476 | 0.40057 | 0.51216 | 0.73534 | 0.91846 | 1.1559 | 1.3763 | 1.8341 | 2.2947 | 3.4335 | 4.5866 | 6.867 | 9.176 | 0.0095 | 0.0597 | 6.2842 | 6.045%
1 | 2 | 0 | 0 | [13 empty] | 1000 | 0.14663 | 0.19413 | 0.21065 | 0.24163 | 0.28913 | 0.36968 | 0.53076 | 0.66294 | 0.83435 | 0.99337 | 1.3238 | 1.6563 | 2.4783 | 3.3106 | 4.9565 | 6.6232 | 0.009 | 0.0575 | 6.3889 | 5.82%
2 | 1/0 | 0 | 0 | [13 empty] | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
3 | 3/0 | 0 | 0 | [13 empty] | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
4 | 350 | 0 | 0 | [13 empty] | 2500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
5 | 500 | 0 | 0 | [13 empty] | 3000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
6 | 1000 | 0 | 0 | [13 empty] | Locked Rotor Current
[17 empty] | @208V | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
[17 empty] | @480V | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
1 Phase
Trans
(kVA)
25
50
75
100
[17 empty] | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE |  |  | Three Phase Motor Data |  | Three PH Motor REF | 9 | HP | #N/A
[17 empty] | 1 | 1 |  |  | 1HP | 0.75 | 41.4096 |  |  | LOOKUP | HP | P.F. | REF
[17 empty] | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096 |  |  | 1 | 3 | 0.3 | 11 | SER 1 | 72.5424
[17 empty] | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096 |  |  | 2 | 4.5 | 0.3 | 14 | SER 2 | 72.5424
[17 empty] | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096 |  |  | 3 | 5 | 0.3 | 9 | SER 3 | 72.5424
[17 empty] | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096 |  |  | 4 | 6 | 0.3 |  | SEC 1 | 72.5424
[17 empty] | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096 |  |  | 5 | 7.5 | 0.3 |  |  | 72.5424
[17 empty] | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096 |  |  | 6 | 10 | 0.3 |  |  | 72.5424
[17 empty] | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096 |  |  | 7 | 15 | 0.3 |  |  | 72.5424
[17 empty] | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096 |  |  | 8 | 20 | 0.3 |  |  | 72.5424
[17 empty] | SINGLE PHASE LOOKUPS |  | Single PH Motor REF |  | 5 | HP | #N/A |  |  | 9 | 25 | 0.3 |  |  | 72.5424
[26 empty] | 10 | 30 | 0.3 |  |  | 72.5424
[26 empty] | 11 | 40 | 0.3 |  |  | 72.5424
[26 empty] | 12 | 50 | 0.3 |  |  | 72.5424
[26 empty] | 13 | 60 | 0.3 |  |  | 72.5424
[26 empty] | 14 | 75 | 0.3 |  |  | 72.5424
[26 empty] | 15 | 100 | 0.3 |  |  | 72.5424
[26 empty] | 16 | 150 | 0.3 |  |  | 72.5424
[26 empty] | 17 | 200 | 0.3 |  |  | 72.5424
[26 empty] | 18 | 250 | 0.3 |  |  | 72.5424
[26 empty] | 19 | 300 | 0.3 |  |  | 72.5424
[26 empty] | 20 | 400 | 0.3 |  |  | 72.5424
[26 empty] | 21 | 500 | 0.3 |  |  | 72.5424
[26 empty] | 22 | 600 | 0.3 |  |  | 72.5424
[26 empty] | 23 | 700 | 0.3 |  |  | 72.5424
[26 empty] | 24 | 800 | 0.3 |  |  | 72.5424
[26 empty] | 25 | 900 | 0.3 |  |  | 72.5424
[26 empty] | 26 | 1000 | 0.3 |  |  | 72.5424
[26 empty] | 27 | 1200 | 0.3 |  |  | 72.5424
[26 empty] | 28 | 1500 | 0.3 |  |  | 72.5424

## UGVDROP6 (hidden)
[17 empty] | Ampicity | Check
Transformer | Trans Kw | [10 empty] | CONDUCTOR DATA DESIGN MANUAL |  |  |  |  | 1 PH | OK
15 | #REF! | [7 empty] | Wire Ref | 1 | ALUMINUM CABLES OHMS / 1000 FT |  |  |  | Volt Drop | Amp Check | 3 PH | #N/A
15 | 0 | [7 empty] | Volt Drop | 0 | SIZE | R | X | Z |  | 1 through 7 | 7 through 12
75 | 0 | [8 empty] | 1 | 2 | 0.267 | 0.0238 | 0.25067 | 0 | OK | NO
[10 empty] | 2 | 1/0 | 0.168 | 0.0241 | 0.1617 | 0 | OK | NO
[9 empty] | 1 | 3 | 3/0 | 0.105 | 0.0226 | 0.10435 | 0 | OK | NO
[9 empty] | 2 | 4 | 350 | 0.0505 | 0.0215 | 0.054822 | 0 | OK | NO
PF | ANGLE |  | 1-PH = 1 | SYSTEM |  | Cable Demand | KW |  | 3 | 5 | 500 | 0.0354 | 0.0207 | 0.040883 | 0 | OK | NO
0.9 | 25.8419 |  | 3-PH = 3 | 1 |  |  | 0 |  | 4 | 6 | 1000 | 0.0177 | 0.0199 | 0.024604 | 0 | OK | NO
VOLTAGE |  |  | RUN |  | FEET |  | L-AMPS |  |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C
120 | 240 |  | 1 |  | 0 |  | 0 |  |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | 600 Volt Secondary Aluminum Cable, DB Conduit (Direct Buried)
|  |  | IF 3 PH | [7 empty] | SIZE | R@65C | R@90C | X | Z | R@90C | Z |  | (With 7-1/2 Inches Centerline to Centerline Spacing Between Conduits)
|  |  | 1 | [7 empty] | 2 | 0.31061 | 0.33653 | 0.045 | 0.32249 | 0.2052 | 0.2043 |  | Cable Size | Conduit | Number of | Number of Runs
[11 empty] | 1 | 0.24432 | 0.26471 | 0.046 | 0.25829 | 0.1623 | 0.16612 |  | Size | Size | Conductors | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Single-Phase Transformers |  |  |  | Three-Phase Transformers | [6 empty] | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.2094 | 0.1334 | 0.13924 |  | 1000 | 5"DB | 3-1/C | 605 | 1104 | 1527 | 1892 | 2335 | 2526 | 2821 | 3080 | 3339 | 3550 | 3707 | 3828
[11 empty] | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.16944 | 0.1028 | 0.11126 |  | 500 | 4"DB | 3-1/C | 397 | 736 | 1029 | 1288 | 1595 | 1746 | 1953 | 2144 | 2313 | 2470 | 2607 | 2712
kVA |  | 15 |  | kVA |  | 75 |  |  |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.13724 | 0.0825 | 0.092557 |  | 350 | 3"DB | 2-1/C | 318 | 600 | 852 | 1076 | 1285 | 1482 | 1673 | 1840 | 2016 | 2160 | 2266 | 2376
Percentage Load |  | 111.1% |  | Percentage Load |  | N/A |  |  |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.11354 | 0.0653 | 0.076641 |  | 350 | 3"DB | 3-1/C | 313 | 586 | 822 | 1036 | 1230 | 1416 | 1589 | 1760 | 1908 | 2040 | 2145 | 2232
%Transformer Volt Drop |  | 2.3 |  | %Transformer Volt Drop |  | 0 |  |  |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.098578 | 0.0552 | 0.067551 |  | 3/0 | 2"DB | 2-1/C | 202 | 386 | 552 | 704 | 875 | 984 | 1113 | 1232 | 1250 | 1440 | 1518 | 1608
Load on Transformer |  | 15 | KW |  |  | 0 | KW |  |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075795 | 0.0404 | 0.053796 |  | 3/0 | 3"DB | 3-1/C | 199 | 376 | 534 | 676 | 810 | 936 | 1057 | 1160 | 1269 | 1350 | 1419 | 1500
[11 empty] | 500 | 0.042235 | 0.04576 | 0.039 | 0.058184 | 0.0289 | 0.04301 |  | 1/0 | 2"DB | 2-1/C | 152 | 292 | 420 | 536 | 645 | 750 | 854 | 944 | 1044 | 1130 | 1188 | 1248
[11 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.043965 | 0.0199 | 0.034474 |  | #2 | 2"DB | 2-1/C | 113 | 218 | 315 | 404 | 490 | 570 | 651 | 720 | 792 | 860 | 913 | 960
[11 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.037873 | 0.0157 | 0.030258 |  | #8 | 1"DB | 1/C | 47 | 92 | 135 | 176 | 215 | 252 | 287 | 320 | 306 | 380 | 407 | 432
Ampacity OK |  | ALUMINUM CABLES |  |  |  | COPPER CABLES
Yes or No | Yes or No |  |  |  | TRANS. + CABLE |  |  | TRANS. + CABLE |  |  |  | 0.023 | 0.024115 |  | 0.077 | 0.080732
1-7 Runs | 8-12 Runs | SIZE | V - DROP | % DROP | %V-DROP | V - DROP | % DROP | V-DROP
OK | NO | 2 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Single Phase Padmount Transformer Size
|  | 1 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [11 empty] | kVA
OK | NO | 1/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Percentage | 15 | 25 | Number of Runs 1: 50; Number of Runs 2: 75; Number of Runs 3: 100; Number of Runs 4: 167; Number of Runs 5: Under 50% Loading
|  | 2/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 50% | 1 | 1 | Number of Runs 1: 1; Number of Runs 2: 0.9; Number of Runs 3: 0.9; Number of Runs 4: 1; Number of Runs 6: #N/A
OK | NO | 3/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 60% | 1.2 | 1.2 | Number of Runs 1: 1.2; Number of Runs 2: 1.1; Number of Runs 3: 1; Number of Runs 4: 1.2; Number of Runs 5: Over 50% Loading
|  | 4/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 70% | 1.5 | 1.4 | Number of Runs 1: 1.4; Number of Runs 2: 1.3; Number of Runs 3: 1.2; Number of Runs 4: 1.4; Number of Runs 6: 2.3
|  | 250 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 50 |  | 80% | 1.7 | 1.6 | Number of Runs 1: 1.6; Number of Runs 2: 1.5; Number of Runs 3: 1.4; Number of Runs 4: 1.6
OK | NO | 350 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 90% | 1.9 | 1.8 | Number of Runs 1: 1.8; Number of Runs 2: 1.6; Number of Runs 3: 1.6; Number of Runs 4: 1.8
OK | NO | 500 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | #VALUE! |  | 100% | 2.1 | 2 | Number of Runs 1: 1.8; Number of Runs 2: 1.8; Number of Runs 3: 1.7; Number of Runs 4: 2
|  | 750 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 60% |  | 110% | 2.3 | 2.2 | Number of Runs 1: 2; Number of Runs 2: 2; Number of Runs 3: 1.9; Number of Runs 4: 2.2
OK | NO | 1000 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 0 |  | 120% | 2.5 | 2.4 | Number of Runs 1: 2.2; Number of Runs 2: 2.2; Number of Runs 3: 2.1; Number of Runs 4: 2.4
[17 empty] | 0 |  | 130% | 2.7 | 2.6 | Number of Runs 1: 2.4; Number of Runs 2: 2.4; Number of Runs 3: 2.3; Number of Runs 4: 2.6
[19 empty] | 140% | 2.9 | 2.8 | Number of Runs 1: 2.6; Number of Runs 2: 2.5; Number of Runs 3: 2.4; Number of Runs 4: 2.9
[17 empty] | 1.35 |  | 150% | 3.1 | 3 | Number of Runs 1: 2.8; Number of Runs 2: 2.7; Number of Runs 3: 2.6; Number of Runs 4: 3.1
[17 empty] | 1 |  | 160% | 3.3 | 3.2 | Number of Runs 1: 2.9; Number of Runs 2: 2.9; Number of Runs 3: 2.8; Number of Runs 4: 3.3
Number of Runs | [16 empty] | 50kVA |  | 170% | 3.5 | 3.4 | Number of Runs 1: 3; Number of Runs 2: 3.1; Number of Runs 3: 3.3; Number of Runs 4: 3.6
1 | [16 empty] | 70%
2 | [16 empty] | #N/A |  | 120/208V Three-Phase Padmount Transformer Size
3 | [18 empty] | Transformer | Kva
4 | [18 empty] | Loading | 45 | 75 | Number of Runs 1: 150; Number of Runs 2: 225; Number of Runs 3: 300; Number of Runs 4: 500; Number of Runs 5: 750; Number of Runs 6: 1000
5 | [18 empty] | 50% | 1.3 | 1.13 | Number of Runs 1: 0.89; Number of Runs 2: 0.91; Number of Runs 3: 0.98; Number of Runs 4: 1.54; Number of Runs 5: 2.03; Number of Runs 6: 1.9
6 | [18 empty] | 60% | 1.6 | 1.35 | Number of Runs 1: 1.07; Number of Runs 2: 1.1; Number of Runs 3: 1.17; Number of Runs 4: 1.8; Number of Runs 5: 2.43; Number of Runs 6: 2.33
7 | [18 empty] | 70% | 1.8 | 1.58 | Number of Runs 1: 1.2; Number of Runs 2: 1.3; Number of Runs 3: 1.37; Number of Runs 4: 2.1; Number of Runs 5: 2.84; Number of Runs 6: 2.72
8 | [18 empty] | 80% | 2.1 | 1.81 | Number of Runs 1: 1.43; Number of Runs 2: 1.46; Number of Runs 3: 1.56; Number of Runs 4: 2.4; Number of Runs 5: 3.2; Number of Runs 6: 3
9 | [18 empty] | 90% | 2.4 | 2.03 | Number of Runs 1: 1.6; Number of Runs 2: 1.64; Number of Runs 3: 1.76; Number of Runs 4: 2.7; Number of Runs 5: 3.6; Number of Runs 6: 3.4
10 | [18 empty] | 100% | 2.6 | 2.26 | Number of Runs 1: 1.78; Number of Runs 2: 1.83; Number of Runs 3: 1.9; Number of Runs 4: 3; Number of Runs 5: 4; Number of Runs 6: 3.8
11 | [18 empty] | 110% | 2.9 | 2.48 | Number of Runs 1: 1.96; Number of Runs 2: 2.01; Number of Runs 3: 2.1; Number of Runs 4: 3.3; Number of Runs 5: 4.3; Number of Runs 6: 4.2
12 | [18 empty] | 120% | 3.2 | 2.71 | Number of Runs 1: 2.14; Number of Runs 2: 2.2; Number of Runs 3: 2.3; Number of Runs 4: 3.6; Number of Runs 5: 4.7; Number of Runs 6: 4.6
[19 empty] | 130% | 3.4 | 2.94 | Number of Runs 1: 2.39; Number of Runs 2: 2.49; Number of Runs 3: 2.72; Number of Runs 4: 4; Number of Runs 5: 5.4; Number of Runs 6: 5.2
[19 empty] | 140% | 3.7 | 3.16 | Number of Runs 1: 2.57; Number of Runs 2: 2.68; Number of Runs 3: 2.93; Number of Runs 4: 4.44; Number of Runs 5: 5.9; Number of Runs 6: 5.6
[19 empty] | 150% | 4 | 3.69 | Number of Runs 1: 2.91; Number of Runs 2: 3.07; Number of Runs 3: 3.37; Number of Runs 4: 5; Number of Runs 5: 6.8; Number of Runs 6: 6.5; Number of Runs 7: Under 50% Loading
#N/A
Over 50% Loading
[19 empty] | 277/480V Three-Phase Padmount Transformer Size |  |  | Number of Runs 8: 0
[19 empty] | Transformer | Kva
[19 empty] | Loading | 75 | 150 | 225 | 300 | 500 | 750 | 1000 | 1500 | 2000 | 2500 | 3000
[19 empty] | 50% | 1.07 | 0.92 | 0.72 | 0.96 | 0.93 | 1.93 | 1.9 | 1.9 | 1.8 | 1.8 | 1.9
[19 empty] | 60% | 1.29 | 1.1 | 0.87 | 1.15 | 1.12 | 2.32 | 2.34 | 2.34 | 2.2 | 2.2 | 2.2
[19 empty] | 70% | 1.5 | 1.3 | 1.01 | 1.3 | 1.3 | 2.6 | 2.73 | 2.6 | 2.63 | 2.6 | 2.6
[19 empty] | 80% | 1.72 | 1.47 | 1.16 | 1.54 | 1.49 | 3 | 3 | 3 | 2.9 | 3.04 | 3
[19 empty] | 90% | 1.93 | 1.65 | 1.3 | 1.73 | 1.68 | 3.4 | 3.4 | 3.4 | 3.3 | 3.3 | 3.3
[19 empty] | 100% | 2.1 | 1.84 | 1.4 | 1.92 | 1.86 | 3.8 | 3.8 | 3.8 | 3.7 | 3.7 | 3.7
[19 empty] | 110% | 2.36 | 2.02 | 1.59 | 2.11 | 2 | 4.1 | 4.2 | 4.2 | 4 | 4.1 | 4.1
[19 empty] | 120% | 2.58 | 2.21 | 1.73 | 2.31 | 2.24 | 4.5 | 4.6 | 4.5 | 4.4 | 4.4 | 4.4
[19 empty] | 130% | 2.79 | 2.5 | 1.88 | 2.6 | 2.5 | 5.2 | 5.2 | 5.3 | 5.1 | 5.2 | 5.2
[19 empty] | 140% | 3.01 | 2.6 | 2.1 | 2.8 | 2.7 | 5.6 | 5.6 | 5.7 | 5.5 | 5.6 | 5.7
[19 empty] | 150% | 3.5 | 3 | 2.4 | 3.3 | 3.1 | 6.4 | 65 | 6.5 | 6.3 | 6.4 | 6.5
2

## UGFLCKER6 (hidden)
[33 empty] | 15 | 2.1 | 1.7 | 1.2 | updated 17th Feb. 2000 with table 5 of 5413.7
[33 empty] | 25 | 2 | 1.6 | 1.2
[33 empty] | 50 | 2.1 | 1.3 | 1.7
[33 empty] | 75 | 2 | 1.1 | 1.8 | 1.051 | 1.751
[33 empty] | 100 | 2.2 | 1.1 | 1.9
[16 empty] | LRC VALUES (updated 5 FEB 1998) | [15 empty] | Single Phase kVA | 167 | 2.3 | 1.1 | 2
[17 empty] | SINGLE-PHASE MOTOR SIZES IN HP | [15 empty] | 45 | 2.7153 | 1.91 | 1.93
[16 empty] | VOLTAGE | 1 | 1.5 | 2 | [13 empty] | 75 | 2.2888 | 1.72 | 1.51 | 1.62 | 1.46
[16 empty] | 120 | 46 | 69 | 92 | [13 empty] | 150 | 1.916 | 1.14 | 1.54
[33 empty] | 225 | 1.9462 | 1.19 | 1.54
[10 empty] | CONDUCTOR DATA DESIGN MANUAL | [22 empty] | 300 | 2.2897 | 1.02 | 2.05
PF | ANGLE | 1-PH = 1 | # OF PHASES | HP | 1Ph-LRC | 1Ph-XKMR% |  |  | ALUMINUM CABLES OHMS / 1000 FT | [23 empty] | 500 | 4.5034 | 0.81 | 4.43
0.75 | 41.4096 | 3-PH = 3 | 1 | 4.5 | 103 | 3.4093 | 1.7 | 1-Ph | SIZE | R | X | Z | L-AMPS |  |  | LRC VALUES (updated 5 FEB 1998) | [16 empty] | 750 | 6.0451 | 0.95 | 5.97
[5 empty] | 3Ph-LRC |  | #N/A | 3-Ph | 2 | 0.267 | 0.0238 | 0.21599 | 103 |  |  |  | SINGLE-PHASE MOTOR SIZES IN HORSE POWER | [15 empty] | 1000 | 5.82 | 0.9 | 5.75
[5 empty] | n/a |  | X |  | 1/0 | 0.168 | 0.0241 | 0.14194 |  |  |  | VOLTAGE | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 10 | [7 empty] | 1500 | 0 | 0 | 0
VOLTAGE |  | RUN | FEET | KW | XFMR KVA | 3Ph-XFMR % | 1.2 | 1-Ph | 3/0 | 0.105 | 0.0226 | 0.093698 |  |  |  | 240 | 27 | 34 | 46 | 69 | 103 | 115 | 140 | 175 | 218 | [7 empty] | 2000 | 0 | 0 | 0
120 | 240 | 1 | 0 | 18.54 | 15 | 0 | #N/A |  | 350 | 0.0505 | 0.0215 | 0.052096 | [20 empty] | 2500 | 0 | 0 | 0
[9 empty] | 500 | 0.0354 | 0.0207 | 0.040242 | [20 empty] | 3000 | 0 | 0 | 0
ALUMINUM CABLES |  |  |  | COPPER CABLES | [27 empty] | Three Phase kVA | Three Phase kVA | Z% | R% | X%
| CABLE | CABLE | *TOTAL% | CABLE | CABLE | *TOTAL% |  |  | 1000 | 0.0177 | 0.0199 | 0.026438 | [20 empty] | updated 17th Feb. 2000 with table 9 of 5413.7
SIZE | (VOLTS) | ( % ) | FLICKER | (VOLTS) | ( % ) | FLICKER |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C | [6 empty] | LRC VALUES (updated 31dec1997)
2 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | MOTOR SIZES IN HORSE POWER
1 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | SIZE | R@65C | R@90C | X | Z | R@90C | Z | VOLTAGE | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200
1/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 2 | 0.31061 | 0.33653 | 0.045 | 0.28216 | 0.2052 | 0.18366 | 208 | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
2/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 1 | 0.24432 | 0.26471 | 0.046 | 0.22896 | 0.1623 | 0.15215 | 240 | 64 | 85 | 92 | 106 | 127 | 162 | 232 | 290 | 365 | 435 | 580 | 725 | 1085 | 1450 | 2170
3/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.18762 | 0.1334 | 0.12915 | 480 | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
4/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.15403 | 0.1028 | 0.10554
250 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.12689 | 0.0825 | 0.089655
350 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.10684 | 0.0653 | 0.076094
500 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.094374 | 0.0552 | 0.068519
750 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075091 | 0.0404 | 0.056758 |  | 3 Phase | Three-Phase Motor (Sized in HP) | [15 empty] | Transformer Data |  | X/R
1000 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 500 | 0.042235 | 0.04576 | 0.039 | 0.060116 | 0.0289 | 0.047471 |  | Trans | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200 | R | X | Ratio | Z%
[9 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.047969 | 0.0199 | 0.04006 |  | 45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.0191 | 0.0193 | 1.0105 | 2.715%
[9 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.042594 | 0.0157 | 0.036248 |  | 75 | 0.66522 | 0.88072 | 0.95567 | 1.0962 | 1.3117 | 1.6771 | 2.4079 | 3.0076 | 3.7852 | 4.5066 | 6.0057 | 7.5142 | 11.2432 | 15.019 | 22.4864 | 30.0474 | 0.0172 | 0.0151 | 0.87791 | 2.289%
WITH REDUCED LRC TO 770A OR 50HP |  |  |  | *TOTAL FLICKER = CABLE (%) + XMFR (%) | [12 empty] | 150 | 0.3078 | 0.40751 | 0.44219 | 0.54094 | 0.60693 | 0.776 | 1.1141 | 1.3916 | 1.7514 | 2.0852 | 2.7789 | 3.4768 | 5.2022 | 6.9493 | 10.4045 | 13.903 | 0.0114 | 0.0154 | 1.3509 | 1.916%
[10 empty] | 0.023 | 0.024115 |  | 0.077 | 0.080732 |  |  | 225 | 0.20691 | 0.27393 | 0.29724 | 0.34096 | 0.40798 | 0.52163 | 0.74894 | 0.93544 | 1.1773 | 1.4017 | 1.868 | 2.3372 | 3.497 | 4.6714 | 6.994 | 9.3457 | 0.0119 | 0.0154 | 1.2941 | 1.946%
[17 empty] | 300 | 0.19214 | 0.25438 | 0.27603 | 0.31663 | 0.37887 | 0.48441 | 0.69549 | 0.86869 | 1.0933 | 1.3017 | 1.7347 | 2.1704 | 3.2474 | 4.338 | 6.4949 | 8.6788 | 0.0102 | 0.0205 | 2.0098 | 2.29%
Lookup Value |  | 0 | [14 empty] | 500 | 0.22773 | 0.3015 | 0.32716 | 0.37527 | 0.44904 | 0.57413 | 0.82432 | 1.0296 | 1.2958 | 1.5428 | 2.056 | 2.5724 | 3.8489 | 5.1415 | 7.6979 | 10.2863 | 0.0081 | 0.0443 | 5.4691 | 4.503%
Lookup | Wire | Volatge Drop | % Volatge Drop | [13 empty] | 750 | 0.20315 | 0.26896 | 0.29185 | 0.33476 | 0.40057 | 0.51216 | 0.73534 | 0.91846 | 1.1559 | 1.3763 | 1.8341 | 2.2947 | 3.4335 | 4.5866 | 6.867 | 9.176 | 0.0095 | 0.0597 | 6.2842 | 6.045%
1 | 2 | 0 | 0 | [13 empty] | 1000 | 0.14663 | 0.19413 | 0.21065 | 0.24163 | 0.28913 | 0.36968 | 0.53076 | 0.66294 | 0.83435 | 0.99337 | 1.3238 | 1.6563 | 2.4783 | 3.3106 | 4.9565 | 6.6232 | 0.009 | 0.0575 | 6.3889 | 5.82%
2 | 1/0 | 0 | 0 | [13 empty] | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
3 | 3/0 | 0 | 0 | [13 empty] | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
4 | 350 | 0 | 0 | [13 empty] | 2500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
5 | 500 | 0 | 0 | [13 empty] | 3000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
6 | 1000 | 0 | 0 | [13 empty] | Locked Rotor Current
[17 empty] | @208V | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
[17 empty] | @480V | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
1 Phase
Trans
(kVA)
25
50
75
100
[17 empty] | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE |  |  | Three Phase Motor Data |  | Three PH Motor REF | 9 | HP | #N/A
[17 empty] | 1 | 1 |  |  | 1HP | 0.75 | 41.4096 |  |  | LOOKUP | HP | P.F. | REF
[17 empty] | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096 |  |  | 1 | 3 | 0.3 | 11 | SER 1 | 72.5424
[17 empty] | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096 |  |  | 2 | 4.5 | 0.3 | 14 | SER 2 | 72.5424
[17 empty] | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096 |  |  | 3 | 5 | 0.3 | 9 | SER 3 | 72.5424
[17 empty] | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096 |  |  | 4 | 6 | 0.3 |  | SEC 1 | 72.5424
[17 empty] | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096 |  |  | 5 | 7.5 | 0.3 |  |  | 72.5424
[17 empty] | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096 |  |  | 6 | 10 | 0.3 |  |  | 72.5424
[17 empty] | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096 |  |  | 7 | 15 | 0.3 |  |  | 72.5424
[17 empty] | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096 |  |  | 8 | 20 | 0.3 |  |  | 72.5424
[17 empty] | SINGLE PHASE LOOKUPS |  | Single PH Motor REF |  | 5 | HP | #N/A |  |  | 9 | 25 | 0.3 |  |  | 72.5424
[26 empty] | 10 | 30 | 0.3 |  |  | 72.5424
[26 empty] | 11 | 40 | 0.3 |  |  | 72.5424
[26 empty] | 12 | 50 | 0.3 |  |  | 72.5424
[26 empty] | 13 | 60 | 0.3 |  |  | 72.5424
[26 empty] | 14 | 75 | 0.3 |  |  | 72.5424
[26 empty] | 15 | 100 | 0.3 |  |  | 72.5424
[26 empty] | 16 | 150 | 0.3 |  |  | 72.5424
[26 empty] | 17 | 200 | 0.3 |  |  | 72.5424
[26 empty] | 18 | 250 | 0.3 |  |  | 72.5424
[26 empty] | 19 | 300 | 0.3 |  |  | 72.5424
[26 empty] | 20 | 400 | 0.3 |  |  | 72.5424
[26 empty] | 21 | 500 | 0.3 |  |  | 72.5424
[26 empty] | 22 | 600 | 0.3 |  |  | 72.5424
[26 empty] | 23 | 700 | 0.3 |  |  | 72.5424
[26 empty] | 24 | 800 | 0.3 |  |  | 72.5424
[26 empty] | 25 | 900 | 0.3 |  |  | 72.5424
[26 empty] | 26 | 1000 | 0.3 |  |  | 72.5424
[26 empty] | 27 | 1200 | 0.3 |  |  | 72.5424
[26 empty] | 28 | 1500 | 0.3 |  |  | 72.5424

## UGVDROP7 (hidden)
[17 empty] | Ampicity | Check
Transformer | Trans Kw | [10 empty] | CONDUCTOR DATA DESIGN MANUAL |  |  |  |  | 1 PH | OK
15 | #REF! | [7 empty] | Wire Ref | 1 | ALUMINUM CABLES OHMS / 1000 FT |  |  |  | Volt Drop | Amp Check | 3 PH | #N/A
15 | 0 | [7 empty] | Volt Drop | 0 | SIZE | R | X | Z |  | 1 through 7 | 7 through 12
75 | 0 | [8 empty] | 1 | 2 | 0.267 | 0.0238 | 0.25067 | 0 | OK | NO
[10 empty] | 2 | 1/0 | 0.168 | 0.0241 | 0.1617 | 0 | OK | NO
[9 empty] | 1 | 3 | 3/0 | 0.105 | 0.0226 | 0.10435 | 0 | OK | NO
[9 empty] | 2 | 4 | 350 | 0.0505 | 0.0215 | 0.054822 | 0 | OK | NO
PF | ANGLE |  | 1-PH = 1 | SYSTEM |  | Cable Demand | KW |  | 3 | 5 | 500 | 0.0354 | 0.0207 | 0.040883 | 0 | OK | NO
0.9 | 25.8419 |  | 3-PH = 3 | 1 |  |  | 0 |  | 4 | 6 | 1000 | 0.0177 | 0.0199 | 0.024604 | 0 | OK | NO
VOLTAGE |  |  | RUN |  | FEET |  | L-AMPS |  |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C
120 | 240 |  | 1 |  | 0 |  | 0 |  |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | 600 Volt Secondary Aluminum Cable, DB Conduit (Direct Buried)
|  |  | IF 3 PH | [7 empty] | SIZE | R@65C | R@90C | X | Z | R@90C | Z |  | (With 7-1/2 Inches Centerline to Centerline Spacing Between Conduits)
|  |  | 1 | [7 empty] | 2 | 0.31061 | 0.33653 | 0.045 | 0.32249 | 0.2052 | 0.2043 |  | Cable Size | Conduit | Number of | Number of Runs
[11 empty] | 1 | 0.24432 | 0.26471 | 0.046 | 0.25829 | 0.1623 | 0.16612 |  | Size | Size | Conductors | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Single-Phase Transformers |  |  |  | Three-Phase Transformers | [6 empty] | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.2094 | 0.1334 | 0.13924 |  | 1000 | 5"DB | 3-1/C | 605 | 1104 | 1527 | 1892 | 2335 | 2526 | 2821 | 3080 | 3339 | 3550 | 3707 | 3828
[11 empty] | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.16944 | 0.1028 | 0.11126 |  | 500 | 4"DB | 3-1/C | 397 | 736 | 1029 | 1288 | 1595 | 1746 | 1953 | 2144 | 2313 | 2470 | 2607 | 2712
kVA |  | 15 |  | kVA |  | 75 |  |  |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.13724 | 0.0825 | 0.092557 |  | 350 | 3"DB | 2-1/C | 318 | 600 | 852 | 1076 | 1285 | 1482 | 1673 | 1840 | 2016 | 2160 | 2266 | 2376
Percentage Load |  | 111.1% |  | Percentage Load |  | N/A |  |  |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.11354 | 0.0653 | 0.076641 |  | 350 | 3"DB | 3-1/C | 313 | 586 | 822 | 1036 | 1230 | 1416 | 1589 | 1760 | 1908 | 2040 | 2145 | 2232
%Transformer Volt Drop |  | 2.3 |  | %Transformer Volt Drop |  | 0 |  |  |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.098578 | 0.0552 | 0.067551 |  | 3/0 | 2"DB | 2-1/C | 202 | 386 | 552 | 704 | 875 | 984 | 1113 | 1232 | 1250 | 1440 | 1518 | 1608
Load on Transformer |  | 15 | KW |  |  | 0 | KW |  |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075795 | 0.0404 | 0.053796 |  | 3/0 | 3"DB | 3-1/C | 199 | 376 | 534 | 676 | 810 | 936 | 1057 | 1160 | 1269 | 1350 | 1419 | 1500
[11 empty] | 500 | 0.042235 | 0.04576 | 0.039 | 0.058184 | 0.0289 | 0.04301 |  | 1/0 | 2"DB | 2-1/C | 152 | 292 | 420 | 536 | 645 | 750 | 854 | 944 | 1044 | 1130 | 1188 | 1248
[11 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.043965 | 0.0199 | 0.034474 |  | #2 | 2"DB | 2-1/C | 113 | 218 | 315 | 404 | 490 | 570 | 651 | 720 | 792 | 860 | 913 | 960
[11 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.037873 | 0.0157 | 0.030258 |  | #8 | 1"DB | 1/C | 47 | 92 | 135 | 176 | 215 | 252 | 287 | 320 | 306 | 380 | 407 | 432
Ampacity OK |  | ALUMINUM CABLES |  |  |  | COPPER CABLES
Yes or No | Yes or No |  |  |  | TRANS. + CABLE |  |  | TRANS. + CABLE |  |  |  | 0.023 | 0.024115 |  | 0.077 | 0.080732
1-7 Runs | 8-12 Runs | SIZE | V - DROP | % DROP | %V-DROP | V - DROP | % DROP | V-DROP
OK | NO | 2 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Single Phase Padmount Transformer Size
|  | 1 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [11 empty] | kVA
OK | NO | 1/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Percentage | 15 | 25 | Number of Runs 1: 50; Number of Runs 2: 75; Number of Runs 3: 100; Number of Runs 4: 167; Number of Runs 5: Under 50% Loading
|  | 2/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 50% | 1 | 1 | Number of Runs 1: 1; Number of Runs 2: 0.9; Number of Runs 3: 0.9; Number of Runs 4: 1; Number of Runs 6: #N/A
OK | NO | 3/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 60% | 1.2 | 1.2 | Number of Runs 1: 1.2; Number of Runs 2: 1.1; Number of Runs 3: 1; Number of Runs 4: 1.2; Number of Runs 5: Over 50% Loading
|  | 4/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 70% | 1.5 | 1.4 | Number of Runs 1: 1.4; Number of Runs 2: 1.3; Number of Runs 3: 1.2; Number of Runs 4: 1.4; Number of Runs 6: 2.3
|  | 250 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 50 |  | 80% | 1.7 | 1.6 | Number of Runs 1: 1.6; Number of Runs 2: 1.5; Number of Runs 3: 1.4; Number of Runs 4: 1.6
OK | NO | 350 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 90% | 1.9 | 1.8 | Number of Runs 1: 1.8; Number of Runs 2: 1.6; Number of Runs 3: 1.6; Number of Runs 4: 1.8
OK | NO | 500 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | #VALUE! |  | 100% | 2.1 | 2 | Number of Runs 1: 1.8; Number of Runs 2: 1.8; Number of Runs 3: 1.7; Number of Runs 4: 2
|  | 750 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 60% |  | 110% | 2.3 | 2.2 | Number of Runs 1: 2; Number of Runs 2: 2; Number of Runs 3: 1.9; Number of Runs 4: 2.2
OK | NO | 1000 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 0 |  | 120% | 2.5 | 2.4 | Number of Runs 1: 2.2; Number of Runs 2: 2.2; Number of Runs 3: 2.1; Number of Runs 4: 2.4
[17 empty] | 0 |  | 130% | 2.7 | 2.6 | Number of Runs 1: 2.4; Number of Runs 2: 2.4; Number of Runs 3: 2.3; Number of Runs 4: 2.6
[19 empty] | 140% | 2.9 | 2.8 | Number of Runs 1: 2.6; Number of Runs 2: 2.5; Number of Runs 3: 2.4; Number of Runs 4: 2.9
[17 empty] | 1.35 |  | 150% | 3.1 | 3 | Number of Runs 1: 2.8; Number of Runs 2: 2.7; Number of Runs 3: 2.6; Number of Runs 4: 3.1
[17 empty] | 1 |  | 160% | 3.3 | 3.2 | Number of Runs 1: 2.9; Number of Runs 2: 2.9; Number of Runs 3: 2.8; Number of Runs 4: 3.3
Number of Runs | [16 empty] | 50kVA |  | 170% | 3.5 | 3.4 | Number of Runs 1: 3; Number of Runs 2: 3.1; Number of Runs 3: 3.3; Number of Runs 4: 3.6
1 | [16 empty] | 70%
2 | [16 empty] | #N/A |  | 120/208V Three-Phase Padmount Transformer Size
3 | [18 empty] | Transformer | Kva
4 | [18 empty] | Loading | 45 | 75 | Number of Runs 1: 150; Number of Runs 2: 225; Number of Runs 3: 300; Number of Runs 4: 500; Number of Runs 5: 750; Number of Runs 6: 1000
5 | [18 empty] | 50% | 1.3 | 1.13 | Number of Runs 1: 0.89; Number of Runs 2: 0.91; Number of Runs 3: 0.98; Number of Runs 4: 1.54; Number of Runs 5: 2.03; Number of Runs 6: 1.9
6 | [18 empty] | 60% | 1.6 | 1.35 | Number of Runs 1: 1.07; Number of Runs 2: 1.1; Number of Runs 3: 1.17; Number of Runs 4: 1.8; Number of Runs 5: 2.43; Number of Runs 6: 2.33
7 | [18 empty] | 70% | 1.8 | 1.58 | Number of Runs 1: 1.2; Number of Runs 2: 1.3; Number of Runs 3: 1.37; Number of Runs 4: 2.1; Number of Runs 5: 2.84; Number of Runs 6: 2.72
8 | [18 empty] | 80% | 2.1 | 1.81 | Number of Runs 1: 1.43; Number of Runs 2: 1.46; Number of Runs 3: 1.56; Number of Runs 4: 2.4; Number of Runs 5: 3.2; Number of Runs 6: 3
9 | [18 empty] | 90% | 2.4 | 2.03 | Number of Runs 1: 1.6; Number of Runs 2: 1.64; Number of Runs 3: 1.76; Number of Runs 4: 2.7; Number of Runs 5: 3.6; Number of Runs 6: 3.4
10 | [18 empty] | 100% | 2.6 | 2.26 | Number of Runs 1: 1.78; Number of Runs 2: 1.83; Number of Runs 3: 1.9; Number of Runs 4: 3; Number of Runs 5: 4; Number of Runs 6: 3.8
11 | [18 empty] | 110% | 2.9 | 2.48 | Number of Runs 1: 1.96; Number of Runs 2: 2.01; Number of Runs 3: 2.1; Number of Runs 4: 3.3; Number of Runs 5: 4.3; Number of Runs 6: 4.2
12 | [18 empty] | 120% | 3.2 | 2.71 | Number of Runs 1: 2.14; Number of Runs 2: 2.2; Number of Runs 3: 2.3; Number of Runs 4: 3.6; Number of Runs 5: 4.7; Number of Runs 6: 4.6
[19 empty] | 130% | 3.4 | 2.94 | Number of Runs 1: 2.39; Number of Runs 2: 2.49; Number of Runs 3: 2.72; Number of Runs 4: 4; Number of Runs 5: 5.4; Number of Runs 6: 5.2
[19 empty] | 140% | 3.7 | 3.16 | Number of Runs 1: 2.57; Number of Runs 2: 2.68; Number of Runs 3: 2.93; Number of Runs 4: 4.44; Number of Runs 5: 5.9; Number of Runs 6: 5.6
[19 empty] | 150% | 4 | 3.69 | Number of Runs 1: 2.91; Number of Runs 2: 3.07; Number of Runs 3: 3.37; Number of Runs 4: 5; Number of Runs 5: 6.8; Number of Runs 6: 6.5; Number of Runs 7: Under 50% Loading
#N/A
Over 50% Loading
[19 empty] | 277/480V Three-Phase Padmount Transformer Size |  |  | Number of Runs 8: 0
[19 empty] | Transformer | Kva
[19 empty] | Loading | 75 | 150 | 225 | 300 | 500 | 750 | 1000 | 1500 | 2000 | 2500 | 3000
[19 empty] | 50% | 1.07 | 0.92 | 0.72 | 0.96 | 0.93 | 1.93 | 1.9 | 1.9 | 1.8 | 1.8 | 1.9
[19 empty] | 60% | 1.29 | 1.1 | 0.87 | 1.15 | 1.12 | 2.32 | 2.34 | 2.34 | 2.2 | 2.2 | 2.2
[19 empty] | 70% | 1.5 | 1.3 | 1.01 | 1.3 | 1.3 | 2.6 | 2.73 | 2.6 | 2.63 | 2.6 | 2.6
[19 empty] | 80% | 1.72 | 1.47 | 1.16 | 1.54 | 1.49 | 3 | 3 | 3 | 2.9 | 3.04 | 3
[19 empty] | 90% | 1.93 | 1.65 | 1.3 | 1.73 | 1.68 | 3.4 | 3.4 | 3.4 | 3.3 | 3.3 | 3.3
[19 empty] | 100% | 2.1 | 1.84 | 1.4 | 1.92 | 1.86 | 3.8 | 3.8 | 3.8 | 3.7 | 3.7 | 3.7
[19 empty] | 110% | 2.36 | 2.02 | 1.59 | 2.11 | 2 | 4.1 | 4.2 | 4.2 | 4 | 4.1 | 4.1
[19 empty] | 120% | 2.58 | 2.21 | 1.73 | 2.31 | 2.24 | 4.5 | 4.6 | 4.5 | 4.4 | 4.4 | 4.4
[19 empty] | 130% | 2.79 | 2.5 | 1.88 | 2.6 | 2.5 | 5.2 | 5.2 | 5.3 | 5.1 | 5.2 | 5.2
[19 empty] | 140% | 3.01 | 2.6 | 2.1 | 2.8 | 2.7 | 5.6 | 5.6 | 5.7 | 5.5 | 5.6 | 5.7
[19 empty] | 150% | 3.5 | 3 | 2.4 | 3.3 | 3.1 | 6.4 | 65 | 6.5 | 6.3 | 6.4 | 6.5
2

## UGFLCKER7 (hidden)
[33 empty] | 15 | 2.1 | 1.7 | 1.2 | updated 17th Feb. 2000 with table 5 of 5413.7
[33 empty] | 25 | 2 | 1.6 | 1.2
[33 empty] | 50 | 2.1 | 1.3 | 1.7
[33 empty] | 75 | 2 | 1.1 | 1.8 | 1.051 | 1.751
[33 empty] | 100 | 2.2 | 1.1 | 1.9
[16 empty] | LRC VALUES (updated 5 FEB 1998) | [15 empty] | Single Phase kVA | 167 | 2.3 | 1.1 | 2
[17 empty] | SINGLE-PHASE MOTOR SIZES IN HP | [15 empty] | 45 | 2.7153 | 1.91 | 1.93
[16 empty] | VOLTAGE | 1 | 1.5 | 2 | [13 empty] | 75 | 2.2888 | 1.72 | 1.51 | 1.62 | 1.46
[16 empty] | 120 | 46 | 69 | 92 | [13 empty] | 150 | 1.916 | 1.14 | 1.54
[33 empty] | 225 | 1.9462 | 1.19 | 1.54
[10 empty] | CONDUCTOR DATA DESIGN MANUAL | [22 empty] | 300 | 2.2897 | 1.02 | 2.05
PF | ANGLE | 1-PH = 1 | # OF PHASES | HP | 1Ph-LRC | 1Ph-XKMR% |  |  | ALUMINUM CABLES OHMS / 1000 FT | [23 empty] | 500 | 4.5034 | 0.81 | 4.43
0.75 | 41.4096 | 3-PH = 3 | 1 | 4.5 | 103 | 3.4093 | 1.7 | 1-Ph | SIZE | R | X | Z | L-AMPS |  |  | LRC VALUES (updated 5 FEB 1998) | [16 empty] | 750 | 6.0451 | 0.95 | 5.97
[5 empty] | 3Ph-LRC |  | #N/A | 3-Ph | 2 | 0.267 | 0.0238 | 0.21599 | 103 |  |  |  | SINGLE-PHASE MOTOR SIZES IN HORSE POWER | [15 empty] | 1000 | 5.82 | 0.9 | 5.75
[5 empty] | n/a |  | X |  | 1/0 | 0.168 | 0.0241 | 0.14194 |  |  |  | VOLTAGE | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 10 | [7 empty] | 1500 | 0 | 0 | 0
VOLTAGE |  | RUN | FEET | KW | XFMR KVA | 3Ph-XFMR % | 1.2 | 1-Ph | 3/0 | 0.105 | 0.0226 | 0.093698 |  |  |  | 240 | 27 | 34 | 46 | 69 | 103 | 115 | 140 | 175 | 218 | [7 empty] | 2000 | 0 | 0 | 0
120 | 240 | 1 | 0 | 18.54 | 15 | 0 | #N/A |  | 350 | 0.0505 | 0.0215 | 0.052096 | [20 empty] | 2500 | 0 | 0 | 0
[9 empty] | 500 | 0.0354 | 0.0207 | 0.040242 | [20 empty] | 3000 | 0 | 0 | 0
ALUMINUM CABLES |  |  |  | COPPER CABLES | [27 empty] | Three Phase kVA | Three Phase kVA | Z% | R% | X%
| CABLE | CABLE | *TOTAL% | CABLE | CABLE | *TOTAL% |  |  | 1000 | 0.0177 | 0.0199 | 0.026438 | [20 empty] | updated 17th Feb. 2000 with table 9 of 5413.7
SIZE | (VOLTS) | ( % ) | FLICKER | (VOLTS) | ( % ) | FLICKER |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C | [6 empty] | LRC VALUES (updated 31dec1997)
2 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | MOTOR SIZES IN HORSE POWER
1 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | SIZE | R@65C | R@90C | X | Z | R@90C | Z | VOLTAGE | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200
1/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 2 | 0.31061 | 0.33653 | 0.045 | 0.28216 | 0.2052 | 0.18366 | 208 | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
2/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 1 | 0.24432 | 0.26471 | 0.046 | 0.22896 | 0.1623 | 0.15215 | 240 | 64 | 85 | 92 | 106 | 127 | 162 | 232 | 290 | 365 | 435 | 580 | 725 | 1085 | 1450 | 2170
3/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.18762 | 0.1334 | 0.12915 | 480 | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
4/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.15403 | 0.1028 | 0.10554
250 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.12689 | 0.0825 | 0.089655
350 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.10684 | 0.0653 | 0.076094
500 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.094374 | 0.0552 | 0.068519
750 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075091 | 0.0404 | 0.056758 |  | 3 Phase | Three-Phase Motor (Sized in HP) | [15 empty] | Transformer Data |  | X/R
1000 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 500 | 0.042235 | 0.04576 | 0.039 | 0.060116 | 0.0289 | 0.047471 |  | Trans | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200 | R | X | Ratio | Z%
[9 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.047969 | 0.0199 | 0.04006 |  | 45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.0191 | 0.0193 | 1.0105 | 2.715%
[9 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.042594 | 0.0157 | 0.036248 |  | 75 | 0.66522 | 0.88072 | 0.95567 | 1.0962 | 1.3117 | 1.6771 | 2.4079 | 3.0076 | 3.7852 | 4.5066 | 6.0057 | 7.5142 | 11.2432 | 15.019 | 22.4864 | 30.0474 | 0.0172 | 0.0151 | 0.87791 | 2.289%
WITH REDUCED LRC TO 770A OR 50HP |  |  |  | *TOTAL FLICKER = CABLE (%) + XMFR (%) | [12 empty] | 150 | 0.3078 | 0.40751 | 0.44219 | 0.54094 | 0.60693 | 0.776 | 1.1141 | 1.3916 | 1.7514 | 2.0852 | 2.7789 | 3.4768 | 5.2022 | 6.9493 | 10.4045 | 13.903 | 0.0114 | 0.0154 | 1.3509 | 1.916%
[10 empty] | 0.023 | 0.024115 |  | 0.077 | 0.080732 |  |  | 225 | 0.20691 | 0.27393 | 0.29724 | 0.34096 | 0.40798 | 0.52163 | 0.74894 | 0.93544 | 1.1773 | 1.4017 | 1.868 | 2.3372 | 3.497 | 4.6714 | 6.994 | 9.3457 | 0.0119 | 0.0154 | 1.2941 | 1.946%
[17 empty] | 300 | 0.19214 | 0.25438 | 0.27603 | 0.31663 | 0.37887 | 0.48441 | 0.69549 | 0.86869 | 1.0933 | 1.3017 | 1.7347 | 2.1704 | 3.2474 | 4.338 | 6.4949 | 8.6788 | 0.0102 | 0.0205 | 2.0098 | 2.29%
Lookup Value |  | 0 | [14 empty] | 500 | 0.22773 | 0.3015 | 0.32716 | 0.37527 | 0.44904 | 0.57413 | 0.82432 | 1.0296 | 1.2958 | 1.5428 | 2.056 | 2.5724 | 3.8489 | 5.1415 | 7.6979 | 10.2863 | 0.0081 | 0.0443 | 5.4691 | 4.503%
Lookup | Wire | Volatge Drop | % Volatge Drop | [13 empty] | 750 | 0.20315 | 0.26896 | 0.29185 | 0.33476 | 0.40057 | 0.51216 | 0.73534 | 0.91846 | 1.1559 | 1.3763 | 1.8341 | 2.2947 | 3.4335 | 4.5866 | 6.867 | 9.176 | 0.0095 | 0.0597 | 6.2842 | 6.045%
1 | 2 | 0 | 0 | [13 empty] | 1000 | 0.14663 | 0.19413 | 0.21065 | 0.24163 | 0.28913 | 0.36968 | 0.53076 | 0.66294 | 0.83435 | 0.99337 | 1.3238 | 1.6563 | 2.4783 | 3.3106 | 4.9565 | 6.6232 | 0.009 | 0.0575 | 6.3889 | 5.82%
2 | 1/0 | 0 | 0 | [13 empty] | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
3 | 3/0 | 0 | 0 | [13 empty] | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
4 | 350 | 0 | 0 | [13 empty] | 2500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
5 | 500 | 0 | 0 | [13 empty] | 3000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
6 | 1000 | 0 | 0 | [13 empty] | Locked Rotor Current
[17 empty] | @208V | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
[17 empty] | @480V | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
1 Phase
Trans
(kVA)
25
50
75
100
[17 empty] | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE |  |  | Three Phase Motor Data |  | Three PH Motor REF | 9 | HP | #N/A
[17 empty] | 1 | 1 |  |  | 1HP | 0.75 | 41.4096 |  |  | LOOKUP | HP | P.F. | REF
[17 empty] | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096 |  |  | 1 | 3 | 0.3 | 11 | SER 1 | 72.5424
[17 empty] | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096 |  |  | 2 | 4.5 | 0.3 | 14 | SER 2 | 72.5424
[17 empty] | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096 |  |  | 3 | 5 | 0.3 | 9 | SER 3 | 72.5424
[17 empty] | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096 |  |  | 4 | 6 | 0.3 |  | SEC 1 | 72.5424
[17 empty] | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096 |  |  | 5 | 7.5 | 0.3 |  |  | 72.5424
[17 empty] | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096 |  |  | 6 | 10 | 0.3 |  |  | 72.5424
[17 empty] | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096 |  |  | 7 | 15 | 0.3 |  |  | 72.5424
[17 empty] | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096 |  |  | 8 | 20 | 0.3 |  |  | 72.5424
[17 empty] | SINGLE PHASE LOOKUPS |  | Single PH Motor REF |  | 5 | HP | #N/A |  |  | 9 | 25 | 0.3 |  |  | 72.5424
[26 empty] | 10 | 30 | 0.3 |  |  | 72.5424
[26 empty] | 11 | 40 | 0.3 |  |  | 72.5424
[26 empty] | 12 | 50 | 0.3 |  |  | 72.5424
[26 empty] | 13 | 60 | 0.3 |  |  | 72.5424
[26 empty] | 14 | 75 | 0.3 |  |  | 72.5424
[26 empty] | 15 | 100 | 0.3 |  |  | 72.5424
[26 empty] | 16 | 150 | 0.3 |  |  | 72.5424
[26 empty] | 17 | 200 | 0.3 |  |  | 72.5424
[26 empty] | 18 | 250 | 0.3 |  |  | 72.5424
[26 empty] | 19 | 300 | 0.3 |  |  | 72.5424
[26 empty] | 20 | 400 | 0.3 |  |  | 72.5424
[26 empty] | 21 | 500 | 0.3 |  |  | 72.5424
[26 empty] | 22 | 600 | 0.3 |  |  | 72.5424
[26 empty] | 23 | 700 | 0.3 |  |  | 72.5424
[26 empty] | 24 | 800 | 0.3 |  |  | 72.5424
[26 empty] | 25 | 900 | 0.3 |  |  | 72.5424
[26 empty] | 26 | 1000 | 0.3 |  |  | 72.5424
[26 empty] | 27 | 1200 | 0.3 |  |  | 72.5424
[26 empty] | 28 | 1500 | 0.3 |  |  | 72.5424

## UGVDROP8 (hidden)
[17 empty] | Ampicity | Check
Transformer | Trans Kw | [10 empty] | CONDUCTOR DATA DESIGN MANUAL |  |  |  |  | 1 PH | OK
15 | #REF! | [7 empty] | Wire Ref | 1 | ALUMINUM CABLES OHMS / 1000 FT |  |  |  | Volt Drop | Amp Check | 3 PH | #N/A
15 | 0 | [7 empty] | Volt Drop | 0 | SIZE | R | X | Z |  | 1 through 7 | 7 through 12
75 | 0 | [8 empty] | 1 | 2 | 0.267 | 0.0238 | 0.25067 | 0 | OK | NO
[10 empty] | 2 | 1/0 | 0.168 | 0.0241 | 0.1617 | 0 | OK | NO
[9 empty] | 1 | 3 | 3/0 | 0.105 | 0.0226 | 0.10435 | 0 | OK | NO
[9 empty] | 2 | 4 | 350 | 0.0505 | 0.0215 | 0.054822 | 0 | OK | NO
PF | ANGLE |  | 1-PH = 1 | SYSTEM |  | Cable Demand | KW |  | 3 | 5 | 500 | 0.0354 | 0.0207 | 0.040883 | 0 | OK | NO
0.9 | 25.8419 |  | 3-PH = 3 | 1 |  |  | 0 |  | 4 | 6 | 1000 | 0.0177 | 0.0199 | 0.024604 | 0 | OK | NO
VOLTAGE |  |  | RUN |  | FEET |  | L-AMPS |  |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C
120 | 240 |  | 1 |  | 0 |  | 0 |  |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | 600 Volt Secondary Aluminum Cable, DB Conduit (Direct Buried)
|  |  | IF 3 PH | [7 empty] | SIZE | R@65C | R@90C | X | Z | R@90C | Z |  | (With 7-1/2 Inches Centerline to Centerline Spacing Between Conduits)
|  |  | 1 | [7 empty] | 2 | 0.31061 | 0.33653 | 0.045 | 0.32249 | 0.2052 | 0.2043 |  | Cable Size | Conduit | Number of | Number of Runs
[11 empty] | 1 | 0.24432 | 0.26471 | 0.046 | 0.25829 | 0.1623 | 0.16612 |  | Size | Size | Conductors | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Single-Phase Transformers |  |  |  | Three-Phase Transformers | [6 empty] | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.2094 | 0.1334 | 0.13924 |  | 1000 | 5"DB | 3-1/C | 605 | 1104 | 1527 | 1892 | 2335 | 2526 | 2821 | 3080 | 3339 | 3550 | 3707 | 3828
[11 empty] | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.16944 | 0.1028 | 0.11126 |  | 500 | 4"DB | 3-1/C | 397 | 736 | 1029 | 1288 | 1595 | 1746 | 1953 | 2144 | 2313 | 2470 | 2607 | 2712
kVA |  | 15 |  | kVA |  | 75 |  |  |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.13724 | 0.0825 | 0.092557 |  | 350 | 3"DB | 2-1/C | 318 | 600 | 852 | 1076 | 1285 | 1482 | 1673 | 1840 | 2016 | 2160 | 2266 | 2376
Percentage Load |  | 111.1% |  | Percentage Load |  | N/A |  |  |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.11354 | 0.0653 | 0.076641 |  | 350 | 3"DB | 3-1/C | 313 | 586 | 822 | 1036 | 1230 | 1416 | 1589 | 1760 | 1908 | 2040 | 2145 | 2232
%Transformer Volt Drop |  | 2.3 |  | %Transformer Volt Drop |  | 0 |  |  |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.098578 | 0.0552 | 0.067551 |  | 3/0 | 2"DB | 2-1/C | 202 | 386 | 552 | 704 | 875 | 984 | 1113 | 1232 | 1250 | 1440 | 1518 | 1608
Load on Transformer |  | 15 | KW |  |  | 0 | KW |  |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075795 | 0.0404 | 0.053796 |  | 3/0 | 3"DB | 3-1/C | 199 | 376 | 534 | 676 | 810 | 936 | 1057 | 1160 | 1269 | 1350 | 1419 | 1500
[11 empty] | 500 | 0.042235 | 0.04576 | 0.039 | 0.058184 | 0.0289 | 0.04301 |  | 1/0 | 2"DB | 2-1/C | 152 | 292 | 420 | 536 | 645 | 750 | 854 | 944 | 1044 | 1130 | 1188 | 1248
[11 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.043965 | 0.0199 | 0.034474 |  | #2 | 2"DB | 2-1/C | 113 | 218 | 315 | 404 | 490 | 570 | 651 | 720 | 792 | 860 | 913 | 960
[11 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.037873 | 0.0157 | 0.030258 |  | #8 | 1"DB | 1/C | 47 | 92 | 135 | 176 | 215 | 252 | 287 | 320 | 306 | 380 | 407 | 432
Ampacity OK |  | ALUMINUM CABLES |  |  |  | COPPER CABLES
Yes or No | Yes or No |  |  |  | TRANS. + CABLE |  |  | TRANS. + CABLE |  |  |  | 0.023 | 0.024115 |  | 0.077 | 0.080732
1-7 Runs | 8-12 Runs | SIZE | V - DROP | % DROP | %V-DROP | V - DROP | % DROP | V-DROP
OK | NO | 2 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Single Phase Padmount Transformer Size
|  | 1 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [11 empty] | kVA
OK | NO | 1/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Percentage | 15 | 25 | Number of Runs 1: 50; Number of Runs 2: 75; Number of Runs 3: 100; Number of Runs 4: 167; Number of Runs 5: Under 50% Loading
|  | 2/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 50% | 1 | 1 | Number of Runs 1: 1; Number of Runs 2: 0.9; Number of Runs 3: 0.9; Number of Runs 4: 1; Number of Runs 6: #N/A
OK | NO | 3/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 60% | 1.2 | 1.2 | Number of Runs 1: 1.2; Number of Runs 2: 1.1; Number of Runs 3: 1; Number of Runs 4: 1.2; Number of Runs 5: Over 50% Loading
|  | 4/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 70% | 1.5 | 1.4 | Number of Runs 1: 1.4; Number of Runs 2: 1.3; Number of Runs 3: 1.2; Number of Runs 4: 1.4; Number of Runs 6: 2.3
|  | 250 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 50 |  | 80% | 1.7 | 1.6 | Number of Runs 1: 1.6; Number of Runs 2: 1.5; Number of Runs 3: 1.4; Number of Runs 4: 1.6
OK | NO | 350 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 90% | 1.9 | 1.8 | Number of Runs 1: 1.8; Number of Runs 2: 1.6; Number of Runs 3: 1.6; Number of Runs 4: 1.8
OK | NO | 500 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | #VALUE! |  | 100% | 2.1 | 2 | Number of Runs 1: 1.8; Number of Runs 2: 1.8; Number of Runs 3: 1.7; Number of Runs 4: 2
|  | 750 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 60% |  | 110% | 2.3 | 2.2 | Number of Runs 1: 2; Number of Runs 2: 2; Number of Runs 3: 1.9; Number of Runs 4: 2.2
OK | NO | 1000 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 0 |  | 120% | 2.5 | 2.4 | Number of Runs 1: 2.2; Number of Runs 2: 2.2; Number of Runs 3: 2.1; Number of Runs 4: 2.4
[17 empty] | 0 |  | 130% | 2.7 | 2.6 | Number of Runs 1: 2.4; Number of Runs 2: 2.4; Number of Runs 3: 2.3; Number of Runs 4: 2.6
[19 empty] | 140% | 2.9 | 2.8 | Number of Runs 1: 2.6; Number of Runs 2: 2.5; Number of Runs 3: 2.4; Number of Runs 4: 2.9
[17 empty] | 1.35 |  | 150% | 3.1 | 3 | Number of Runs 1: 2.8; Number of Runs 2: 2.7; Number of Runs 3: 2.6; Number of Runs 4: 3.1
[17 empty] | 1 |  | 160% | 3.3 | 3.2 | Number of Runs 1: 2.9; Number of Runs 2: 2.9; Number of Runs 3: 2.8; Number of Runs 4: 3.3
Number of Runs | [16 empty] | 50kVA |  | 170% | 3.5 | 3.4 | Number of Runs 1: 3; Number of Runs 2: 3.1; Number of Runs 3: 3.3; Number of Runs 4: 3.6
1 | [16 empty] | 70%
2 | [16 empty] | #N/A |  | 120/208V Three-Phase Padmount Transformer Size
3 | [18 empty] | Transformer | Kva
4 | [18 empty] | Loading | 45 | 75 | Number of Runs 1: 150; Number of Runs 2: 225; Number of Runs 3: 300; Number of Runs 4: 500; Number of Runs 5: 750; Number of Runs 6: 1000
5 | [18 empty] | 50% | 1.3 | 1.13 | Number of Runs 1: 0.89; Number of Runs 2: 0.91; Number of Runs 3: 0.98; Number of Runs 4: 1.54; Number of Runs 5: 2.03; Number of Runs 6: 1.9
6 | [18 empty] | 60% | 1.6 | 1.35 | Number of Runs 1: 1.07; Number of Runs 2: 1.1; Number of Runs 3: 1.17; Number of Runs 4: 1.8; Number of Runs 5: 2.43; Number of Runs 6: 2.33
7 | [18 empty] | 70% | 1.8 | 1.58 | Number of Runs 1: 1.2; Number of Runs 2: 1.3; Number of Runs 3: 1.37; Number of Runs 4: 2.1; Number of Runs 5: 2.84; Number of Runs 6: 2.72
8 | [18 empty] | 80% | 2.1 | 1.81 | Number of Runs 1: 1.43; Number of Runs 2: 1.46; Number of Runs 3: 1.56; Number of Runs 4: 2.4; Number of Runs 5: 3.2; Number of Runs 6: 3
9 | [18 empty] | 90% | 2.4 | 2.03 | Number of Runs 1: 1.6; Number of Runs 2: 1.64; Number of Runs 3: 1.76; Number of Runs 4: 2.7; Number of Runs 5: 3.6; Number of Runs 6: 3.4
10 | [18 empty] | 100% | 2.6 | 2.26 | Number of Runs 1: 1.78; Number of Runs 2: 1.83; Number of Runs 3: 1.9; Number of Runs 4: 3; Number of Runs 5: 4; Number of Runs 6: 3.8
11 | [18 empty] | 110% | 2.9 | 2.48 | Number of Runs 1: 1.96; Number of Runs 2: 2.01; Number of Runs 3: 2.1; Number of Runs 4: 3.3; Number of Runs 5: 4.3; Number of Runs 6: 4.2
12 | [18 empty] | 120% | 3.2 | 2.71 | Number of Runs 1: 2.14; Number of Runs 2: 2.2; Number of Runs 3: 2.3; Number of Runs 4: 3.6; Number of Runs 5: 4.7; Number of Runs 6: 4.6
[19 empty] | 130% | 3.4 | 2.94 | Number of Runs 1: 2.39; Number of Runs 2: 2.49; Number of Runs 3: 2.72; Number of Runs 4: 4; Number of Runs 5: 5.4; Number of Runs 6: 5.2
[19 empty] | 140% | 3.7 | 3.16 | Number of Runs 1: 2.57; Number of Runs 2: 2.68; Number of Runs 3: 2.93; Number of Runs 4: 4.44; Number of Runs 5: 5.9; Number of Runs 6: 5.6
[19 empty] | 150% | 4 | 3.69 | Number of Runs 1: 2.91; Number of Runs 2: 3.07; Number of Runs 3: 3.37; Number of Runs 4: 5; Number of Runs 5: 6.8; Number of Runs 6: 6.5; Number of Runs 7: Under 50% Loading
#N/A
Over 50% Loading
[19 empty] | 277/480V Three-Phase Padmount Transformer Size |  |  | Number of Runs 8: 0
[19 empty] | Transformer | Kva
[19 empty] | Loading | 75 | 150 | 225 | 300 | 500 | 750 | 1000 | 1500 | 2000 | 2500 | 3000
[19 empty] | 50% | 1.07 | 0.92 | 0.72 | 0.96 | 0.93 | 1.93 | 1.9 | 1.9 | 1.8 | 1.8 | 1.9
[19 empty] | 60% | 1.29 | 1.1 | 0.87 | 1.15 | 1.12 | 2.32 | 2.34 | 2.34 | 2.2 | 2.2 | 2.2
[19 empty] | 70% | 1.5 | 1.3 | 1.01 | 1.3 | 1.3 | 2.6 | 2.73 | 2.6 | 2.63 | 2.6 | 2.6
[19 empty] | 80% | 1.72 | 1.47 | 1.16 | 1.54 | 1.49 | 3 | 3 | 3 | 2.9 | 3.04 | 3
[19 empty] | 90% | 1.93 | 1.65 | 1.3 | 1.73 | 1.68 | 3.4 | 3.4 | 3.4 | 3.3 | 3.3 | 3.3
[19 empty] | 100% | 2.1 | 1.84 | 1.4 | 1.92 | 1.86 | 3.8 | 3.8 | 3.8 | 3.7 | 3.7 | 3.7
[19 empty] | 110% | 2.36 | 2.02 | 1.59 | 2.11 | 2 | 4.1 | 4.2 | 4.2 | 4 | 4.1 | 4.1
[19 empty] | 120% | 2.58 | 2.21 | 1.73 | 2.31 | 2.24 | 4.5 | 4.6 | 4.5 | 4.4 | 4.4 | 4.4
[19 empty] | 130% | 2.79 | 2.5 | 1.88 | 2.6 | 2.5 | 5.2 | 5.2 | 5.3 | 5.1 | 5.2 | 5.2
[19 empty] | 140% | 3.01 | 2.6 | 2.1 | 2.8 | 2.7 | 5.6 | 5.6 | 5.7 | 5.5 | 5.6 | 5.7
[19 empty] | 150% | 3.5 | 3 | 2.4 | 3.3 | 3.1 | 6.4 | 65 | 6.5 | 6.3 | 6.4 | 6.5
2

## UGFLCKER8 (hidden)
[33 empty] | 15 | 2.1 | 1.7 | 1.2 | updated 17th Feb. 2000 with table 5 of 5413.7
[33 empty] | 25 | 2 | 1.6 | 1.2
[33 empty] | 50 | 2.1 | 1.3 | 1.7
[33 empty] | 75 | 2 | 1.1 | 1.8 | 1.051 | 1.751
[33 empty] | 100 | 2.2 | 1.1 | 1.9
[16 empty] | LRC VALUES (updated 5 FEB 1998) | [15 empty] | Single Phase kVA | 167 | 2.3 | 1.1 | 2
[17 empty] | SINGLE-PHASE MOTOR SIZES IN HP | [15 empty] | 45 | 2.7153 | 1.91 | 1.93
[16 empty] | VOLTAGE | 1 | 1.5 | 2 | [13 empty] | 75 | 2.2888 | 1.72 | 1.51 | 1.62 | 1.46
[16 empty] | 120 | 46 | 69 | 92 | [13 empty] | 150 | 1.916 | 1.14 | 1.54
[33 empty] | 225 | 1.9462 | 1.19 | 1.54
[10 empty] | CONDUCTOR DATA DESIGN MANUAL | [22 empty] | 300 | 2.2897 | 1.02 | 2.05
PF | ANGLE | 1-PH = 1 | # OF PHASES | HP | 1Ph-LRC | 1Ph-XKMR% |  |  | ALUMINUM CABLES OHMS / 1000 FT | [23 empty] | 500 | 4.5034 | 0.81 | 4.43
0.75 | 41.4096 | 3-PH = 3 | 1 | 4.5 | 103 | 3.4093 | 1.7 | 1-Ph | SIZE | R | X | Z | L-AMPS |  |  | LRC VALUES (updated 5 FEB 1998) | [16 empty] | 750 | 6.0451 | 0.95 | 5.97
[5 empty] | 3Ph-LRC |  | #N/A | 3-Ph | 2 | 0.267 | 0.0238 | 0.21599 | 103 |  |  |  | SINGLE-PHASE MOTOR SIZES IN HORSE POWER | [15 empty] | 1000 | 5.82 | 0.9 | 5.75
[5 empty] | n/a |  | X |  | 1/0 | 0.168 | 0.0241 | 0.14194 |  |  |  | VOLTAGE | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 10 | [7 empty] | 1500 | 0 | 0 | 0
VOLTAGE |  | RUN | FEET | KW | XFMR KVA | 3Ph-XFMR % | 1.2 | 1-Ph | 3/0 | 0.105 | 0.0226 | 0.093698 |  |  |  | 240 | 27 | 34 | 46 | 69 | 103 | 115 | 140 | 175 | 218 | [7 empty] | 2000 | 0 | 0 | 0
120 | 240 | 1 | 0 | 18.54 | 15 | 0 | #N/A |  | 350 | 0.0505 | 0.0215 | 0.052096 | [20 empty] | 2500 | 0 | 0 | 0
[9 empty] | 500 | 0.0354 | 0.0207 | 0.040242 | [20 empty] | 3000 | 0 | 0 | 0
ALUMINUM CABLES |  |  |  | COPPER CABLES | [27 empty] | Three Phase kVA | Three Phase kVA | Z% | R% | X%
| CABLE | CABLE | *TOTAL% | CABLE | CABLE | *TOTAL% |  |  | 1000 | 0.0177 | 0.0199 | 0.026438 | [20 empty] | updated 17th Feb. 2000 with table 9 of 5413.7
SIZE | (VOLTS) | ( % ) | FLICKER | (VOLTS) | ( % ) | FLICKER |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C | [6 empty] | LRC VALUES (updated 31dec1997)
2 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | MOTOR SIZES IN HORSE POWER
1 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | SIZE | R@65C | R@90C | X | Z | R@90C | Z | VOLTAGE | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200
1/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 2 | 0.31061 | 0.33653 | 0.045 | 0.28216 | 0.2052 | 0.18366 | 208 | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
2/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 1 | 0.24432 | 0.26471 | 0.046 | 0.22896 | 0.1623 | 0.15215 | 240 | 64 | 85 | 92 | 106 | 127 | 162 | 232 | 290 | 365 | 435 | 580 | 725 | 1085 | 1450 | 2170
3/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.18762 | 0.1334 | 0.12915 | 480 | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
4/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.15403 | 0.1028 | 0.10554
250 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.12689 | 0.0825 | 0.089655
350 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.10684 | 0.0653 | 0.076094
500 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.094374 | 0.0552 | 0.068519
750 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075091 | 0.0404 | 0.056758 |  | 3 Phase | Three-Phase Motor (Sized in HP) | [15 empty] | Transformer Data |  | X/R
1000 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 500 | 0.042235 | 0.04576 | 0.039 | 0.060116 | 0.0289 | 0.047471 |  | Trans | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200 | R | X | Ratio | Z%
[9 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.047969 | 0.0199 | 0.04006 |  | 45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.0191 | 0.0193 | 1.0105 | 2.715%
[9 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.042594 | 0.0157 | 0.036248 |  | 75 | 0.66522 | 0.88072 | 0.95567 | 1.0962 | 1.3117 | 1.6771 | 2.4079 | 3.0076 | 3.7852 | 4.5066 | 6.0057 | 7.5142 | 11.2432 | 15.019 | 22.4864 | 30.0474 | 0.0172 | 0.0151 | 0.87791 | 2.289%
WITH REDUCED LRC TO 770A OR 50HP |  |  |  | *TOTAL FLICKER = CABLE (%) + XMFR (%) | [12 empty] | 150 | 0.3078 | 0.40751 | 0.44219 | 0.54094 | 0.60693 | 0.776 | 1.1141 | 1.3916 | 1.7514 | 2.0852 | 2.7789 | 3.4768 | 5.2022 | 6.9493 | 10.4045 | 13.903 | 0.0114 | 0.0154 | 1.3509 | 1.916%
[10 empty] | 0.023 | 0.024115 |  | 0.077 | 0.080732 |  |  | 225 | 0.20691 | 0.27393 | 0.29724 | 0.34096 | 0.40798 | 0.52163 | 0.74894 | 0.93544 | 1.1773 | 1.4017 | 1.868 | 2.3372 | 3.497 | 4.6714 | 6.994 | 9.3457 | 0.0119 | 0.0154 | 1.2941 | 1.946%
[17 empty] | 300 | 0.19214 | 0.25438 | 0.27603 | 0.31663 | 0.37887 | 0.48441 | 0.69549 | 0.86869 | 1.0933 | 1.3017 | 1.7347 | 2.1704 | 3.2474 | 4.338 | 6.4949 | 8.6788 | 0.0102 | 0.0205 | 2.0098 | 2.29%
Lookup Value |  | 0 | [14 empty] | 500 | 0.22773 | 0.3015 | 0.32716 | 0.37527 | 0.44904 | 0.57413 | 0.82432 | 1.0296 | 1.2958 | 1.5428 | 2.056 | 2.5724 | 3.8489 | 5.1415 | 7.6979 | 10.2863 | 0.0081 | 0.0443 | 5.4691 | 4.503%
Lookup | Wire | Volatge Drop | % Volatge Drop | [13 empty] | 750 | 0.20315 | 0.26896 | 0.29185 | 0.33476 | 0.40057 | 0.51216 | 0.73534 | 0.91846 | 1.1559 | 1.3763 | 1.8341 | 2.2947 | 3.4335 | 4.5866 | 6.867 | 9.176 | 0.0095 | 0.0597 | 6.2842 | 6.045%
1 | 2 | 0 | 0 | [13 empty] | 1000 | 0.14663 | 0.19413 | 0.21065 | 0.24163 | 0.28913 | 0.36968 | 0.53076 | 0.66294 | 0.83435 | 0.99337 | 1.3238 | 1.6563 | 2.4783 | 3.3106 | 4.9565 | 6.6232 | 0.009 | 0.0575 | 6.3889 | 5.82%
2 | 1/0 | 0 | 0 | [13 empty] | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
3 | 3/0 | 0 | 0 | [13 empty] | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
4 | 350 | 0 | 0 | [13 empty] | 2500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
5 | 500 | 0 | 0 | [13 empty] | 3000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
6 | 1000 | 0 | 0 | [13 empty] | Locked Rotor Current
[17 empty] | @208V | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
[17 empty] | @480V | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
1 Phase
Trans
(kVA)
25
50
75
100
[17 empty] | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE |  |  | Three Phase Motor Data |  | Three PH Motor REF | 9 | HP | #N/A
[17 empty] | 1 | 1 |  |  | 1HP | 0.75 | 41.4096 |  |  | LOOKUP | HP | P.F. | REF
[17 empty] | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096 |  |  | 1 | 3 | 0.3 | 11 | SER 1 | 72.5424
[17 empty] | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096 |  |  | 2 | 4.5 | 0.3 | 14 | SER 2 | 72.5424
[17 empty] | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096 |  |  | 3 | 5 | 0.3 | 9 | SER 3 | 72.5424
[17 empty] | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096 |  |  | 4 | 6 | 0.3 |  | SEC 1 | 72.5424
[17 empty] | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096 |  |  | 5 | 7.5 | 0.3 |  |  | 72.5424
[17 empty] | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096 |  |  | 6 | 10 | 0.3 |  |  | 72.5424
[17 empty] | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096 |  |  | 7 | 15 | 0.3 |  |  | 72.5424
[17 empty] | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096 |  |  | 8 | 20 | 0.3 |  |  | 72.5424
[17 empty] | SINGLE PHASE LOOKUPS |  | Single PH Motor REF |  | 5 | HP | #N/A |  |  | 9 | 25 | 0.3 |  |  | 72.5424
[26 empty] | 10 | 30 | 0.3 |  |  | 72.5424
[26 empty] | 11 | 40 | 0.3 |  |  | 72.5424
[26 empty] | 12 | 50 | 0.3 |  |  | 72.5424
[26 empty] | 13 | 60 | 0.3 |  |  | 72.5424
[26 empty] | 14 | 75 | 0.3 |  |  | 72.5424
[26 empty] | 15 | 100 | 0.3 |  |  | 72.5424
[26 empty] | 16 | 150 | 0.3 |  |  | 72.5424
[26 empty] | 17 | 200 | 0.3 |  |  | 72.5424
[26 empty] | 18 | 250 | 0.3 |  |  | 72.5424
[26 empty] | 19 | 300 | 0.3 |  |  | 72.5424
[26 empty] | 20 | 400 | 0.3 |  |  | 72.5424
[26 empty] | 21 | 500 | 0.3 |  |  | 72.5424
[26 empty] | 22 | 600 | 0.3 |  |  | 72.5424
[26 empty] | 23 | 700 | 0.3 |  |  | 72.5424
[26 empty] | 24 | 800 | 0.3 |  |  | 72.5424
[26 empty] | 25 | 900 | 0.3 |  |  | 72.5424
[26 empty] | 26 | 1000 | 0.3 |  |  | 72.5424
[26 empty] | 27 | 1200 | 0.3 |  |  | 72.5424
[26 empty] | 28 | 1500 | 0.3 |  |  | 72.5424

## UGVDROP9 (hidden)
[17 empty] | Ampicity | Check
Transformer | Trans Kw | [10 empty] | CONDUCTOR DATA DESIGN MANUAL |  |  |  |  | 1 PH | OK
15 | #REF! | [7 empty] | Wire Ref | 1 | ALUMINUM CABLES OHMS / 1000 FT |  |  |  | Volt Drop | Amp Check | 3 PH | #N/A
15 | 0 | [7 empty] | Volt Drop | 0 | SIZE | R | X | Z |  | 1 through 7 | 7 through 12
75 | 0 | [8 empty] | 1 | 2 | 0.267 | 0.0238 | 0.25067 | 0 | OK | NO
[10 empty] | 2 | 1/0 | 0.168 | 0.0241 | 0.1617 | 0 | OK | NO
[9 empty] | 1 | 3 | 3/0 | 0.105 | 0.0226 | 0.10435 | 0 | OK | NO
[9 empty] | 2 | 4 | 350 | 0.0505 | 0.0215 | 0.054822 | 0 | OK | NO
PF | ANGLE |  | 1-PH = 1 | SYSTEM |  | Cable Demand | KW |  | 3 | 5 | 500 | 0.0354 | 0.0207 | 0.040883 | 0 | OK | NO
0.9 | 25.8419 |  | 3-PH = 3 | 1 |  |  | 0 |  | 4 | 6 | 1000 | 0.0177 | 0.0199 | 0.024604 | 0 | OK | NO
VOLTAGE |  |  | RUN |  | FEET |  | L-AMPS |  |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C
120 | 240 |  | 1 |  | 0 |  | 0 |  |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | 600 Volt Secondary Aluminum Cable, DB Conduit (Direct Buried)
|  |  | IF 3 PH | [7 empty] | SIZE | R@65C | R@90C | X | Z | R@90C | Z |  | (With 7-1/2 Inches Centerline to Centerline Spacing Between Conduits)
|  |  | 1 | [7 empty] | 2 | 0.31061 | 0.33653 | 0.045 | 0.32249 | 0.2052 | 0.2043 |  | Cable Size | Conduit | Number of | Number of Runs
[11 empty] | 1 | 0.24432 | 0.26471 | 0.046 | 0.25829 | 0.1623 | 0.16612 |  | Size | Size | Conductors | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Single-Phase Transformers |  |  |  | Three-Phase Transformers | [6 empty] | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.2094 | 0.1334 | 0.13924 |  | 1000 | 5"DB | 3-1/C | 605 | 1104 | 1527 | 1892 | 2335 | 2526 | 2821 | 3080 | 3339 | 3550 | 3707 | 3828
[11 empty] | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.16944 | 0.1028 | 0.11126 |  | 500 | 4"DB | 3-1/C | 397 | 736 | 1029 | 1288 | 1595 | 1746 | 1953 | 2144 | 2313 | 2470 | 2607 | 2712
kVA |  | 15 |  | kVA |  | 75 |  |  |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.13724 | 0.0825 | 0.092557 |  | 350 | 3"DB | 2-1/C | 318 | 600 | 852 | 1076 | 1285 | 1482 | 1673 | 1840 | 2016 | 2160 | 2266 | 2376
Percentage Load |  | 111.1% |  | Percentage Load |  | N/A |  |  |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.11354 | 0.0653 | 0.076641 |  | 350 | 3"DB | 3-1/C | 313 | 586 | 822 | 1036 | 1230 | 1416 | 1589 | 1760 | 1908 | 2040 | 2145 | 2232
%Transformer Volt Drop |  | 2.3 |  | %Transformer Volt Drop |  | 0 |  |  |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.098578 | 0.0552 | 0.067551 |  | 3/0 | 2"DB | 2-1/C | 202 | 386 | 552 | 704 | 875 | 984 | 1113 | 1232 | 1250 | 1440 | 1518 | 1608
Load on Transformer |  | 15 | KW |  |  | 0 | KW |  |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075795 | 0.0404 | 0.053796 |  | 3/0 | 3"DB | 3-1/C | 199 | 376 | 534 | 676 | 810 | 936 | 1057 | 1160 | 1269 | 1350 | 1419 | 1500
[11 empty] | 500 | 0.042235 | 0.04576 | 0.039 | 0.058184 | 0.0289 | 0.04301 |  | 1/0 | 2"DB | 2-1/C | 152 | 292 | 420 | 536 | 645 | 750 | 854 | 944 | 1044 | 1130 | 1188 | 1248
[11 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.043965 | 0.0199 | 0.034474 |  | #2 | 2"DB | 2-1/C | 113 | 218 | 315 | 404 | 490 | 570 | 651 | 720 | 792 | 860 | 913 | 960
[11 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.037873 | 0.0157 | 0.030258 |  | #8 | 1"DB | 1/C | 47 | 92 | 135 | 176 | 215 | 252 | 287 | 320 | 306 | 380 | 407 | 432
Ampacity OK |  | ALUMINUM CABLES |  |  |  | COPPER CABLES
Yes or No | Yes or No |  |  |  | TRANS. + CABLE |  |  | TRANS. + CABLE |  |  |  | 0.023 | 0.024115 |  | 0.077 | 0.080732
1-7 Runs | 8-12 Runs | SIZE | V - DROP | % DROP | %V-DROP | V - DROP | % DROP | V-DROP
OK | NO | 2 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Single Phase Padmount Transformer Size
|  | 1 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [11 empty] | kVA
OK | NO | 1/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Percentage | 15 | 25 | Number of Runs 1: 50; Number of Runs 2: 75; Number of Runs 3: 100; Number of Runs 4: 167; Number of Runs 5: Under 50% Loading
|  | 2/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 50% | 1 | 1 | Number of Runs 1: 1; Number of Runs 2: 0.9; Number of Runs 3: 0.9; Number of Runs 4: 1; Number of Runs 6: #N/A
OK | NO | 3/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 60% | 1.2 | 1.2 | Number of Runs 1: 1.2; Number of Runs 2: 1.1; Number of Runs 3: 1; Number of Runs 4: 1.2; Number of Runs 5: Over 50% Loading
|  | 4/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 70% | 1.5 | 1.4 | Number of Runs 1: 1.4; Number of Runs 2: 1.3; Number of Runs 3: 1.2; Number of Runs 4: 1.4; Number of Runs 6: 2.3
|  | 250 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 50 |  | 80% | 1.7 | 1.6 | Number of Runs 1: 1.6; Number of Runs 2: 1.5; Number of Runs 3: 1.4; Number of Runs 4: 1.6
OK | NO | 350 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 90% | 1.9 | 1.8 | Number of Runs 1: 1.8; Number of Runs 2: 1.6; Number of Runs 3: 1.6; Number of Runs 4: 1.8
OK | NO | 500 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | #VALUE! |  | 100% | 2.1 | 2 | Number of Runs 1: 1.8; Number of Runs 2: 1.8; Number of Runs 3: 1.7; Number of Runs 4: 2
|  | 750 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 60% |  | 110% | 2.3 | 2.2 | Number of Runs 1: 2; Number of Runs 2: 2; Number of Runs 3: 1.9; Number of Runs 4: 2.2
OK | NO | 1000 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 0 |  | 120% | 2.5 | 2.4 | Number of Runs 1: 2.2; Number of Runs 2: 2.2; Number of Runs 3: 2.1; Number of Runs 4: 2.4
[17 empty] | 0 |  | 130% | 2.7 | 2.6 | Number of Runs 1: 2.4; Number of Runs 2: 2.4; Number of Runs 3: 2.3; Number of Runs 4: 2.6
[19 empty] | 140% | 2.9 | 2.8 | Number of Runs 1: 2.6; Number of Runs 2: 2.5; Number of Runs 3: 2.4; Number of Runs 4: 2.9
[17 empty] | 1.35 |  | 150% | 3.1 | 3 | Number of Runs 1: 2.8; Number of Runs 2: 2.7; Number of Runs 3: 2.6; Number of Runs 4: 3.1
[17 empty] | 1 |  | 160% | 3.3 | 3.2 | Number of Runs 1: 2.9; Number of Runs 2: 2.9; Number of Runs 3: 2.8; Number of Runs 4: 3.3
[17 empty] | 50kVA |  | 170% | 3.5 | 3.4 | Number of Runs 1: 3; Number of Runs 2: 3.1; Number of Runs 3: 3.3; Number of Runs 4: 3.6
70%
[17 empty] | #N/A |  | 120/208V Three-Phase Padmount Transformer Size
[19 empty] | Transformer | Kva
[19 empty] | Loading | 45 | 75 | Number of Runs 1: 150; Number of Runs 2: 225; Number of Runs 3: 300; Number of Runs 4: 500; Number of Runs 5: 750; Number of Runs 6: 1000
[19 empty] | 50% | 1.3 | 1.13 | Number of Runs 1: 0.89; Number of Runs 2: 0.91; Number of Runs 3: 0.98; Number of Runs 4: 1.54; Number of Runs 5: 2.03; Number of Runs 6: 1.9
[19 empty] | 60% | 1.6 | 1.35 | Number of Runs 1: 1.07; Number of Runs 2: 1.1; Number of Runs 3: 1.17; Number of Runs 4: 1.8; Number of Runs 5: 2.43; Number of Runs 6: 2.33
[19 empty] | 70% | 1.8 | 1.58 | Number of Runs 1: 1.2; Number of Runs 2: 1.3; Number of Runs 3: 1.37; Number of Runs 4: 2.1; Number of Runs 5: 2.84; Number of Runs 6: 2.72
[19 empty] | 80% | 2.1 | 1.81 | Number of Runs 1: 1.43; Number of Runs 2: 1.46; Number of Runs 3: 1.56; Number of Runs 4: 2.4; Number of Runs 5: 3.2; Number of Runs 6: 3
[19 empty] | 90% | 2.4 | 2.03 | Number of Runs 1: 1.6; Number of Runs 2: 1.64; Number of Runs 3: 1.76; Number of Runs 4: 2.7; Number of Runs 5: 3.6; Number of Runs 6: 3.4
[19 empty] | 100% | 2.6 | 2.26 | Number of Runs 1: 1.78; Number of Runs 2: 1.83; Number of Runs 3: 1.9; Number of Runs 4: 3; Number of Runs 5: 4; Number of Runs 6: 3.8
[19 empty] | 110% | 2.9 | 2.48 | Number of Runs 1: 1.96; Number of Runs 2: 2.01; Number of Runs 3: 2.1; Number of Runs 4: 3.3; Number of Runs 5: 4.3; Number of Runs 6: 4.2
[19 empty] | 120% | 3.2 | 2.71 | Number of Runs 1: 2.14; Number of Runs 2: 2.2; Number of Runs 3: 2.3; Number of Runs 4: 3.6; Number of Runs 5: 4.7; Number of Runs 6: 4.6
[19 empty] | 130% | 3.4 | 2.94 | Number of Runs 1: 2.39; Number of Runs 2: 2.49; Number of Runs 3: 2.72; Number of Runs 4: 4; Number of Runs 5: 5.4; Number of Runs 6: 5.2
[19 empty] | 140% | 3.7 | 3.16 | Number of Runs 1: 2.57; Number of Runs 2: 2.68; Number of Runs 3: 2.93; Number of Runs 4: 4.44; Number of Runs 5: 5.9; Number of Runs 6: 5.6
[19 empty] | 150% | 4 | 3.69 | Number of Runs 1: 2.91; Number of Runs 2: 3.07; Number of Runs 3: 3.37; Number of Runs 4: 5; Number of Runs 5: 6.8; Number of Runs 6: 6.5; Number of Runs 7: Under 50% Loading
#N/A
Over 50% Loading
[19 empty] | 277/480V Three-Phase Padmount Transformer Size |  |  | Number of Runs 8: 0
[19 empty] | Transformer | Kva
[19 empty] | Loading | 75 | 150 | 225 | 300 | 500 | 750 | 1000 | 1500 | 2000 | 2500 | 3000
[19 empty] | 50% | 1.07 | 0.92 | 0.72 | 0.96 | 0.93 | 1.93 | 1.9 | 1.9 | 1.8 | 1.8 | 1.9
[19 empty] | 60% | 1.29 | 1.1 | 0.87 | 1.15 | 1.12 | 2.32 | 2.34 | 2.34 | 2.2 | 2.2 | 2.2
[19 empty] | 70% | 1.5 | 1.3 | 1.01 | 1.3 | 1.3 | 2.6 | 2.73 | 2.6 | 2.63 | 2.6 | 2.6
[19 empty] | 80% | 1.72 | 1.47 | 1.16 | 1.54 | 1.49 | 3 | 3 | 3 | 2.9 | 3.04 | 3
[19 empty] | 90% | 1.93 | 1.65 | 1.3 | 1.73 | 1.68 | 3.4 | 3.4 | 3.4 | 3.3 | 3.3 | 3.3
[19 empty] | 100% | 2.1 | 1.84 | 1.4 | 1.92 | 1.86 | 3.8 | 3.8 | 3.8 | 3.7 | 3.7 | 3.7
[19 empty] | 110% | 2.36 | 2.02 | 1.59 | 2.11 | 2 | 4.1 | 4.2 | 4.2 | 4 | 4.1 | 4.1
[19 empty] | 120% | 2.58 | 2.21 | 1.73 | 2.31 | 2.24 | 4.5 | 4.6 | 4.5 | 4.4 | 4.4 | 4.4
[19 empty] | 130% | 2.79 | 2.5 | 1.88 | 2.6 | 2.5 | 5.2 | 5.2 | 5.3 | 5.1 | 5.2 | 5.2
[19 empty] | 140% | 3.01 | 2.6 | 2.1 | 2.8 | 2.7 | 5.6 | 5.6 | 5.7 | 5.5 | 5.6 | 5.7
[19 empty] | 150% | 3.5 | 3 | 2.4 | 3.3 | 3.1 | 6.4 | 65 | 6.5 | 6.3 | 6.4 | 6.5
2

## UGFLCKER9 (hidden)
[33 empty] | 15 | 2.1 | 1.7 | 1.2 | updated 17th Feb. 2000 with table 5 of 5413.7
[33 empty] | 25 | 2 | 1.6 | 1.2
[33 empty] | 50 | 2.1 | 1.3 | 1.7
[33 empty] | 75 | 2 | 1.1 | 1.8 | 1.051 | 1.751
[33 empty] | 100 | 2.2 | 1.1 | 1.9
[16 empty] | LRC VALUES (updated 5 FEB 1998) | [15 empty] | Single Phase kVA | 167 | 2.3 | 1.1 | 2
[17 empty] | SINGLE-PHASE MOTOR SIZES IN HP | [15 empty] | 45 | 2.7153 | 1.91 | 1.93
[16 empty] | VOLTAGE | 1 | 1.5 | 2 | [13 empty] | 75 | 2.2888 | 1.72 | 1.51 | 1.62 | 1.46
[16 empty] | 120 | 46 | 69 | 92 | [13 empty] | 150 | 1.916 | 1.14 | 1.54
[33 empty] | 225 | 1.9462 | 1.19 | 1.54
[10 empty] | CONDUCTOR DATA DESIGN MANUAL | [22 empty] | 300 | 2.2897 | 1.02 | 2.05
PF | ANGLE | 1-PH = 1 | # OF PHASES | HP | 1Ph-LRC | 1Ph-XKMR% |  |  | ALUMINUM CABLES OHMS / 1000 FT | [23 empty] | 500 | 4.5034 | 0.81 | 4.43
0.75 | 41.4096 | 3-PH = 3 | 1 | 4.5 | 103 | 3.4093 | 1.7 | 1-Ph | SIZE | R | X | Z | L-AMPS |  |  | LRC VALUES (updated 5 FEB 1998) | [16 empty] | 750 | 6.0451 | 0.95 | 5.97
[5 empty] | 3Ph-LRC |  | #N/A | 3-Ph | 2 | 0.267 | 0.0238 | 0.21599 | 103 |  |  |  | SINGLE-PHASE MOTOR SIZES IN HORSE POWER | [15 empty] | 1000 | 5.82 | 0.9 | 5.75
[5 empty] | n/a |  | X |  | 1/0 | 0.168 | 0.0241 | 0.14194 |  |  |  | VOLTAGE | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 10 | [7 empty] | 1500 | 0 | 0 | 0
VOLTAGE |  | RUN | FEET | KW | XFMR KVA | 3Ph-XFMR % | 1.2 | 1-Ph | 3/0 | 0.105 | 0.0226 | 0.093698 |  |  |  | 240 | 27 | 34 | 46 | 69 | 103 | 115 | 140 | 175 | 218 | [7 empty] | 2000 | 0 | 0 | 0
120 | 240 | 1 | 0 | 18.54 | 15 | 0 | #N/A |  | 350 | 0.0505 | 0.0215 | 0.052096 | [20 empty] | 2500 | 0 | 0 | 0
[9 empty] | 500 | 0.0354 | 0.0207 | 0.040242 | [20 empty] | 3000 | 0 | 0 | 0
ALUMINUM CABLES |  |  |  | COPPER CABLES | [27 empty] | Three Phase kVA | Three Phase kVA | Z% | R% | X%
| CABLE | CABLE | *TOTAL% | CABLE | CABLE | *TOTAL% |  |  | 1000 | 0.0177 | 0.0199 | 0.026438 | [20 empty] | updated 17th Feb. 2000 with table 9 of 5413.7
SIZE | (VOLTS) | ( % ) | FLICKER | (VOLTS) | ( % ) | FLICKER |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C | [6 empty] | LRC VALUES (updated 31dec1997)
2 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | MOTOR SIZES IN HORSE POWER
1 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | SIZE | R@65C | R@90C | X | Z | R@90C | Z | VOLTAGE | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200
1/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 2 | 0.31061 | 0.33653 | 0.045 | 0.28216 | 0.2052 | 0.18366 | 208 | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
2/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 1 | 0.24432 | 0.26471 | 0.046 | 0.22896 | 0.1623 | 0.15215 | 240 | 64 | 85 | 92 | 106 | 127 | 162 | 232 | 290 | 365 | 435 | 580 | 725 | 1085 | 1450 | 2170
3/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.18762 | 0.1334 | 0.12915 | 480 | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
4/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.15403 | 0.1028 | 0.10554
250 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.12689 | 0.0825 | 0.089655
350 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.10684 | 0.0653 | 0.076094
500 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.094374 | 0.0552 | 0.068519
750 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075091 | 0.0404 | 0.056758 |  | 3 Phase | Three-Phase Motor (Sized in HP) | [15 empty] | Transformer Data |  | X/R
1000 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 500 | 0.042235 | 0.04576 | 0.039 | 0.060116 | 0.0289 | 0.047471 |  | Trans | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200 | R | X | Ratio | Z%
[9 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.047969 | 0.0199 | 0.04006 |  | 45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.0191 | 0.0193 | 1.0105 | 2.715%
[9 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.042594 | 0.0157 | 0.036248 |  | 75 | 0.66522 | 0.88072 | 0.95567 | 1.0962 | 1.3117 | 1.6771 | 2.4079 | 3.0076 | 3.7852 | 4.5066 | 6.0057 | 7.5142 | 11.2432 | 15.019 | 22.4864 | 30.0474 | 0.0172 | 0.0151 | 0.87791 | 2.289%
WITH REDUCED LRC TO 770A OR 50HP |  |  |  | *TOTAL FLICKER = CABLE (%) + XMFR (%) | [12 empty] | 150 | 0.3078 | 0.40751 | 0.44219 | 0.54094 | 0.60693 | 0.776 | 1.1141 | 1.3916 | 1.7514 | 2.0852 | 2.7789 | 3.4768 | 5.2022 | 6.9493 | 10.4045 | 13.903 | 0.0114 | 0.0154 | 1.3509 | 1.916%
[10 empty] | 0.023 | 0.024115 |  | 0.077 | 0.080732 |  |  | 225 | 0.20691 | 0.27393 | 0.29724 | 0.34096 | 0.40798 | 0.52163 | 0.74894 | 0.93544 | 1.1773 | 1.4017 | 1.868 | 2.3372 | 3.497 | 4.6714 | 6.994 | 9.3457 | 0.0119 | 0.0154 | 1.2941 | 1.946%
[17 empty] | 300 | 0.19214 | 0.25438 | 0.27603 | 0.31663 | 0.37887 | 0.48441 | 0.69549 | 0.86869 | 1.0933 | 1.3017 | 1.7347 | 2.1704 | 3.2474 | 4.338 | 6.4949 | 8.6788 | 0.0102 | 0.0205 | 2.0098 | 2.29%
Lookup Value |  | 0 | [14 empty] | 500 | 0.22773 | 0.3015 | 0.32716 | 0.37527 | 0.44904 | 0.57413 | 0.82432 | 1.0296 | 1.2958 | 1.5428 | 2.056 | 2.5724 | 3.8489 | 5.1415 | 7.6979 | 10.2863 | 0.0081 | 0.0443 | 5.4691 | 4.503%
Lookup | Wire | Volatge Drop | % Volatge Drop | [13 empty] | 750 | 0.20315 | 0.26896 | 0.29185 | 0.33476 | 0.40057 | 0.51216 | 0.73534 | 0.91846 | 1.1559 | 1.3763 | 1.8341 | 2.2947 | 3.4335 | 4.5866 | 6.867 | 9.176 | 0.0095 | 0.0597 | 6.2842 | 6.045%
1 | 2 | 0 | 0 | [13 empty] | 1000 | 0.14663 | 0.19413 | 0.21065 | 0.24163 | 0.28913 | 0.36968 | 0.53076 | 0.66294 | 0.83435 | 0.99337 | 1.3238 | 1.6563 | 2.4783 | 3.3106 | 4.9565 | 6.6232 | 0.009 | 0.0575 | 6.3889 | 5.82%
2 | 1/0 | 0 | 0 | [13 empty] | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
3 | 3/0 | 0 | 0 | [13 empty] | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
4 | 350 | 0 | 0 | [13 empty] | 2500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
5 | 500 | 0 | 0 | [13 empty] | 3000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
6 | 1000 | 0 | 0 | [13 empty] | Locked Rotor Current
[17 empty] | @208V | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
[17 empty] | @480V | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
1 Phase
Trans
(kVA)
25
50
75
100
[17 empty] | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE |  |  | Three Phase Motor Data |  | Three PH Motor REF | 9 | HP | #N/A
[17 empty] | 1 | 1 |  |  | 1HP | 0.75 | 41.4096 |  |  | LOOKUP | HP | P.F. | REF
[17 empty] | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096 |  |  | 1 | 3 | 0.3 | 11 | SER 1 | 72.5424
[17 empty] | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096 |  |  | 2 | 4.5 | 0.3 | 14 | SER 2 | 72.5424
[17 empty] | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096 |  |  | 3 | 5 | 0.3 | 9 | SER 3 | 72.5424
[17 empty] | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096 |  |  | 4 | 6 | 0.3 |  | SEC 1 | 72.5424
[17 empty] | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096 |  |  | 5 | 7.5 | 0.3 |  |  | 72.5424
[17 empty] | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096 |  |  | 6 | 10 | 0.3 |  |  | 72.5424
[17 empty] | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096 |  |  | 7 | 15 | 0.3 |  |  | 72.5424
[17 empty] | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096 |  |  | 8 | 20 | 0.3 |  |  | 72.5424
[17 empty] | SINGLE PHASE LOOKUPS |  | Single PH Motor REF |  | 5 | HP | #N/A |  |  | 9 | 25 | 0.3 |  |  | 72.5424
[26 empty] | 10 | 30 | 0.3 |  |  | 72.5424
[26 empty] | 11 | 40 | 0.3 |  |  | 72.5424
[26 empty] | 12 | 50 | 0.3 |  |  | 72.5424
[26 empty] | 13 | 60 | 0.3 |  |  | 72.5424
[26 empty] | 14 | 75 | 0.3 |  |  | 72.5424
[26 empty] | 15 | 100 | 0.3 |  |  | 72.5424
[26 empty] | 16 | 150 | 0.3 |  |  | 72.5424
[26 empty] | 17 | 200 | 0.3 |  |  | 72.5424
[26 empty] | 18 | 250 | 0.3 |  |  | 72.5424
[26 empty] | 19 | 300 | 0.3 |  |  | 72.5424
[26 empty] | 20 | 400 | 0.3 |  |  | 72.5424
[26 empty] | 21 | 500 | 0.3 |  |  | 72.5424
[26 empty] | 22 | 600 | 0.3 |  |  | 72.5424
[26 empty] | 23 | 700 | 0.3 |  |  | 72.5424
[26 empty] | 24 | 800 | 0.3 |  |  | 72.5424
[26 empty] | 25 | 900 | 0.3 |  |  | 72.5424
[26 empty] | 26 | 1000 | 0.3 |  |  | 72.5424
[26 empty] | 27 | 1200 | 0.3 |  |  | 72.5424
[26 empty] | 28 | 1500 | 0.3 |  |  | 72.5424

## UGVDROP10 (hidden)
[17 empty] | Ampicity | Check
Transformer | Trans Kw | [10 empty] | CONDUCTOR DATA DESIGN MANUAL |  |  |  |  | 1 PH | OK
15 | #REF! | [7 empty] | Wire Ref | 1 | ALUMINUM CABLES OHMS / 1000 FT |  |  |  | Volt Drop | Amp Check | 3 PH | #N/A
15 | 0 | [7 empty] | Volt Drop | 0 | SIZE | R | X | Z |  | 1 through 7 | 7 through 12
75 | 0 | [8 empty] | 1 | 2 | 0.267 | 0.0238 | 0.25067 | 0 | OK | NO
[10 empty] | 2 | 1/0 | 0.168 | 0.0241 | 0.1617 | 0 | OK | NO
[9 empty] | 1 | 3 | 3/0 | 0.105 | 0.0226 | 0.10435 | 0 | OK | NO
[9 empty] | 2 | 4 | 350 | 0.0505 | 0.0215 | 0.054822 | 0 | OK | NO
PF | ANGLE |  | 1-PH = 1 | SYSTEM |  | Cable Demand | KW |  | 3 | 5 | 500 | 0.0354 | 0.0207 | 0.040883 | 0 | OK | NO
0.9 | 25.8419 |  | 3-PH = 3 | 1 |  |  | 0 |  | 4 | 6 | 1000 | 0.0177 | 0.0199 | 0.024604 | 0 | OK | NO
VOLTAGE |  |  | RUN |  | FEET |  | L-AMPS |  |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C
120 | 240 |  | 1 |  | 0 |  | 0 |  |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | 600 Volt Secondary Aluminum Cable, DB Conduit (Direct Buried)
|  |  | IF 3 PH | [7 empty] | SIZE | R@65C | R@90C | X | Z | R@90C | Z |  | (With 7-1/2 Inches Centerline to Centerline Spacing Between Conduits)
|  |  | 1 | [7 empty] | 2 | 0.31061 | 0.33653 | 0.045 | 0.32249 | 0.2052 | 0.2043 |  | Cable Size | Conduit | Number of | Number of Runs
[11 empty] | 1 | 0.24432 | 0.26471 | 0.046 | 0.25829 | 0.1623 | 0.16612 |  | Size | Size | Conductors | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Single-Phase Transformers |  |  |  | Three-Phase Transformers | [6 empty] | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.2094 | 0.1334 | 0.13924 |  | 1000 | 5"DB | 3-1/C | 605 | 1104 | 1527 | 1892 | 2335 | 2526 | 2821 | 3080 | 3339 | 3550 | 3707 | 3828
[11 empty] | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.16944 | 0.1028 | 0.11126 |  | 500 | 4"DB | 3-1/C | 397 | 736 | 1029 | 1288 | 1595 | 1746 | 1953 | 2144 | 2313 | 2470 | 2607 | 2712
kVA |  | 15 |  | kVA |  | 75 |  |  |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.13724 | 0.0825 | 0.092557 |  | 350 | 3"DB | 2-1/C | 318 | 600 | 852 | 1076 | 1285 | 1482 | 1673 | 1840 | 2016 | 2160 | 2266 | 2376
Percentage Load |  | 111.1% |  | Percentage Load |  | N/A |  |  |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.11354 | 0.0653 | 0.076641 |  | 350 | 3"DB | 3-1/C | 313 | 586 | 822 | 1036 | 1230 | 1416 | 1589 | 1760 | 1908 | 2040 | 2145 | 2232
%Transformer Volt Drop |  | 2.3 |  | %Transformer Volt Drop |  | 0 |  |  |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.098578 | 0.0552 | 0.067551 |  | 3/0 | 2"DB | 2-1/C | 202 | 386 | 552 | 704 | 875 | 984 | 1113 | 1232 | 1250 | 1440 | 1518 | 1608
Load on Transformer |  | 15 | KW |  |  | 0 | KW |  |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075795 | 0.0404 | 0.053796 |  | 3/0 | 3"DB | 3-1/C | 199 | 376 | 534 | 676 | 810 | 936 | 1057 | 1160 | 1269 | 1350 | 1419 | 1500
[11 empty] | 500 | 0.042235 | 0.04576 | 0.039 | 0.058184 | 0.0289 | 0.04301 |  | 1/0 | 2"DB | 2-1/C | 152 | 292 | 420 | 536 | 645 | 750 | 854 | 944 | 1044 | 1130 | 1188 | 1248
[11 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.043965 | 0.0199 | 0.034474 |  | #2 | 2"DB | 2-1/C | 113 | 218 | 315 | 404 | 490 | 570 | 651 | 720 | 792 | 860 | 913 | 960
[11 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.037873 | 0.0157 | 0.030258 |  | #8 | 1"DB | 1/C | 47 | 92 | 135 | 176 | 215 | 252 | 287 | 320 | 306 | 380 | 407 | 432
Ampacity OK |  | ALUMINUM CABLES |  |  |  | COPPER CABLES
Yes or No | Yes or No |  |  |  | TRANS. + CABLE |  |  | TRANS. + CABLE |  |  |  | 0.023 | 0.024115 |  | 0.077 | 0.080732
1-7 Runs | 8-12 Runs | SIZE | V - DROP | % DROP | %V-DROP | V - DROP | % DROP | V-DROP
OK | NO | 2 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Single Phase Padmount Transformer Size
|  | 1 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [11 empty] | kVA
OK | NO | 1/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Percentage | 15 | 25 | Number of Runs 1: 50; Number of Runs 2: 75; Number of Runs 3: 100; Number of Runs 4: 167; Number of Runs 5: Under 50% Loading
|  | 2/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 50% | 1 | 1 | Number of Runs 1: 1; Number of Runs 2: 0.9; Number of Runs 3: 0.9; Number of Runs 4: 1; Number of Runs 6: #N/A
OK | NO | 3/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 60% | 1.2 | 1.2 | Number of Runs 1: 1.2; Number of Runs 2: 1.1; Number of Runs 3: 1; Number of Runs 4: 1.2; Number of Runs 5: Over 50% Loading
|  | 4/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 70% | 1.5 | 1.4 | Number of Runs 1: 1.4; Number of Runs 2: 1.3; Number of Runs 3: 1.2; Number of Runs 4: 1.4; Number of Runs 6: 2.3
|  | 250 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 50 |  | 80% | 1.7 | 1.6 | Number of Runs 1: 1.6; Number of Runs 2: 1.5; Number of Runs 3: 1.4; Number of Runs 4: 1.6
OK | NO | 350 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 90% | 1.9 | 1.8 | Number of Runs 1: 1.8; Number of Runs 2: 1.6; Number of Runs 3: 1.6; Number of Runs 4: 1.8
OK | NO | 500 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | #VALUE! |  | 100% | 2.1 | 2 | Number of Runs 1: 1.8; Number of Runs 2: 1.8; Number of Runs 3: 1.7; Number of Runs 4: 2
|  | 750 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 60% |  | 110% | 2.3 | 2.2 | Number of Runs 1: 2; Number of Runs 2: 2; Number of Runs 3: 1.9; Number of Runs 4: 2.2
OK | NO | 1000 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 0 |  | 120% | 2.5 | 2.4 | Number of Runs 1: 2.2; Number of Runs 2: 2.2; Number of Runs 3: 2.1; Number of Runs 4: 2.4
[17 empty] | 0 |  | 130% | 2.7 | 2.6 | Number of Runs 1: 2.4; Number of Runs 2: 2.4; Number of Runs 3: 2.3; Number of Runs 4: 2.6
[19 empty] | 140% | 2.9 | 2.8 | Number of Runs 1: 2.6; Number of Runs 2: 2.5; Number of Runs 3: 2.4; Number of Runs 4: 2.9
[17 empty] | 1.35 |  | 150% | 3.1 | 3 | Number of Runs 1: 2.8; Number of Runs 2: 2.7; Number of Runs 3: 2.6; Number of Runs 4: 3.1
[17 empty] | 1 |  | 160% | 3.3 | 3.2 | Number of Runs 1: 2.9; Number of Runs 2: 2.9; Number of Runs 3: 2.8; Number of Runs 4: 3.3
Number of Runs | [16 empty] | 50kVA |  | 170% | 3.5 | 3.4 | Number of Runs 1: 3; Number of Runs 2: 3.1; Number of Runs 3: 3.3; Number of Runs 4: 3.6
1 | [16 empty] | 70%
2 | [16 empty] | #N/A |  | 120/208V Three-Phase Padmount Transformer Size
3 | [18 empty] | Transformer | Kva
4 | [18 empty] | Loading | 45 | 75 | Number of Runs 1: 150; Number of Runs 2: 225; Number of Runs 3: 300; Number of Runs 4: 500; Number of Runs 5: 750; Number of Runs 6: 1000
5 | [18 empty] | 50% | 1.3 | 1.13 | Number of Runs 1: 0.89; Number of Runs 2: 0.91; Number of Runs 3: 0.98; Number of Runs 4: 1.54; Number of Runs 5: 2.03; Number of Runs 6: 1.9
6 | [18 empty] | 60% | 1.6 | 1.35 | Number of Runs 1: 1.07; Number of Runs 2: 1.1; Number of Runs 3: 1.17; Number of Runs 4: 1.8; Number of Runs 5: 2.43; Number of Runs 6: 2.33
7 | [18 empty] | 70% | 1.8 | 1.58 | Number of Runs 1: 1.2; Number of Runs 2: 1.3; Number of Runs 3: 1.37; Number of Runs 4: 2.1; Number of Runs 5: 2.84; Number of Runs 6: 2.72
8 | [18 empty] | 80% | 2.1 | 1.81 | Number of Runs 1: 1.43; Number of Runs 2: 1.46; Number of Runs 3: 1.56; Number of Runs 4: 2.4; Number of Runs 5: 3.2; Number of Runs 6: 3
9 | [18 empty] | 90% | 2.4 | 2.03 | Number of Runs 1: 1.6; Number of Runs 2: 1.64; Number of Runs 3: 1.76; Number of Runs 4: 2.7; Number of Runs 5: 3.6; Number of Runs 6: 3.4
10 | [18 empty] | 100% | 2.6 | 2.26 | Number of Runs 1: 1.78; Number of Runs 2: 1.83; Number of Runs 3: 1.9; Number of Runs 4: 3; Number of Runs 5: 4; Number of Runs 6: 3.8
11 | [18 empty] | 110% | 2.9 | 2.48 | Number of Runs 1: 1.96; Number of Runs 2: 2.01; Number of Runs 3: 2.1; Number of Runs 4: 3.3; Number of Runs 5: 4.3; Number of Runs 6: 4.2
12 | [18 empty] | 120% | 3.2 | 2.71 | Number of Runs 1: 2.14; Number of Runs 2: 2.2; Number of Runs 3: 2.3; Number of Runs 4: 3.6; Number of Runs 5: 4.7; Number of Runs 6: 4.6
[19 empty] | 130% | 3.4 | 2.94 | Number of Runs 1: 2.39; Number of Runs 2: 2.49; Number of Runs 3: 2.72; Number of Runs 4: 4; Number of Runs 5: 5.4; Number of Runs 6: 5.2
[19 empty] | 140% | 3.7 | 3.16 | Number of Runs 1: 2.57; Number of Runs 2: 2.68; Number of Runs 3: 2.93; Number of Runs 4: 4.44; Number of Runs 5: 5.9; Number of Runs 6: 5.6
[19 empty] | 150% | 4 | 3.69 | Number of Runs 1: 2.91; Number of Runs 2: 3.07; Number of Runs 3: 3.37; Number of Runs 4: 5; Number of Runs 5: 6.8; Number of Runs 6: 6.5; Number of Runs 7: Under 50% Loading
#N/A
Over 50% Loading
[19 empty] | 277/480V Three-Phase Padmount Transformer Size |  |  | Number of Runs 8: 0
[19 empty] | Transformer | Kva
[19 empty] | Loading | 75 | 150 | 225 | 300 | 500 | 750 | 1000 | 1500 | 2000 | 2500 | 3000
[19 empty] | 50% | 1.07 | 0.92 | 0.72 | 0.96 | 0.93 | 1.93 | 1.9 | 1.9 | 1.8 | 1.8 | 1.9
[19 empty] | 60% | 1.29 | 1.1 | 0.87 | 1.15 | 1.12 | 2.32 | 2.34 | 2.34 | 2.2 | 2.2 | 2.2
[19 empty] | 70% | 1.5 | 1.3 | 1.01 | 1.3 | 1.3 | 2.6 | 2.73 | 2.6 | 2.63 | 2.6 | 2.6
[19 empty] | 80% | 1.72 | 1.47 | 1.16 | 1.54 | 1.49 | 3 | 3 | 3 | 2.9 | 3.04 | 3
[19 empty] | 90% | 1.93 | 1.65 | 1.3 | 1.73 | 1.68 | 3.4 | 3.4 | 3.4 | 3.3 | 3.3 | 3.3
[19 empty] | 100% | 2.1 | 1.84 | 1.4 | 1.92 | 1.86 | 3.8 | 3.8 | 3.8 | 3.7 | 3.7 | 3.7
[19 empty] | 110% | 2.36 | 2.02 | 1.59 | 2.11 | 2 | 4.1 | 4.2 | 4.2 | 4 | 4.1 | 4.1
[19 empty] | 120% | 2.58 | 2.21 | 1.73 | 2.31 | 2.24 | 4.5 | 4.6 | 4.5 | 4.4 | 4.4 | 4.4
[19 empty] | 130% | 2.79 | 2.5 | 1.88 | 2.6 | 2.5 | 5.2 | 5.2 | 5.3 | 5.1 | 5.2 | 5.2
[19 empty] | 140% | 3.01 | 2.6 | 2.1 | 2.8 | 2.7 | 5.6 | 5.6 | 5.7 | 5.5 | 5.6 | 5.7
[19 empty] | 150% | 3.5 | 3 | 2.4 | 3.3 | 3.1 | 6.4 | 65 | 6.5 | 6.3 | 6.4 | 6.5
2

## UGFLCKER10 (hidden)
[33 empty] | 15 | 2.1 | 1.7 | 1.2 | updated 17th Feb. 2000 with table 5 of 5413.7
[33 empty] | 25 | 2 | 1.6 | 1.2
[33 empty] | 50 | 2.1 | 1.3 | 1.7
[33 empty] | 75 | 2 | 1.1 | 1.8 | 1.051 | 1.751
[33 empty] | 100 | 2.2 | 1.1 | 1.9
[16 empty] | LRC VALUES (updated 5 FEB 1998) | [15 empty] | Single Phase kVA | 167 | 2.3 | 1.1 | 2
[17 empty] | SINGLE-PHASE MOTOR SIZES IN HP | [15 empty] | 45 | 2.7153 | 1.91 | 1.93
[16 empty] | VOLTAGE | 1 | 1.5 | 2 | [13 empty] | 75 | 2.2888 | 1.72 | 1.51 | 1.62 | 1.46
[16 empty] | 120 | 46 | 69 | 92 | [13 empty] | 150 | 1.916 | 1.14 | 1.54
[33 empty] | 225 | 1.9462 | 1.19 | 1.54
[10 empty] | CONDUCTOR DATA DESIGN MANUAL | [22 empty] | 300 | 2.2897 | 1.02 | 2.05
PF | ANGLE | 1-PH = 1 | # OF PHASES | HP | 1Ph-LRC | 1Ph-XKMR% |  |  | ALUMINUM CABLES OHMS / 1000 FT | [23 empty] | 500 | 4.5034 | 0.81 | 4.43
0.75 | 41.4096 | 3-PH = 3 | 1 | 4.5 | 103 | 3.4093 | 1.7 | 1-Ph | SIZE | R | X | Z | L-AMPS |  |  | LRC VALUES (updated 5 FEB 1998) | [16 empty] | 750 | 6.0451 | 0.95 | 5.97
[5 empty] | 3Ph-LRC |  | #N/A | 3-Ph | 2 | 0.267 | 0.0238 | 0.21599 | 103 |  |  |  | SINGLE-PHASE MOTOR SIZES IN HORSE POWER | [15 empty] | 1000 | 5.82 | 0.9 | 5.75
[5 empty] | n/a |  | X |  | 1/0 | 0.168 | 0.0241 | 0.14194 |  |  |  | VOLTAGE | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 10 | [7 empty] | 1500 | 0 | 0 | 0
VOLTAGE |  | RUN | FEET | KW | XFMR KVA | 3Ph-XFMR % | 1.2 | 1-Ph | 3/0 | 0.105 | 0.0226 | 0.093698 |  |  |  | 240 | 27 | 34 | 46 | 69 | 103 | 115 | 140 | 175 | 218 | [7 empty] | 2000 | 0 | 0 | 0
120 | 240 | 1 | 0 | 18.54 | 15 | 0 | #N/A |  | 350 | 0.0505 | 0.0215 | 0.052096 | [20 empty] | 2500 | 0 | 0 | 0
[9 empty] | 500 | 0.0354 | 0.0207 | 0.040242 | [20 empty] | 3000 | 0 | 0 | 0
ALUMINUM CABLES |  |  |  | COPPER CABLES | [27 empty] | Three Phase kVA | Three Phase kVA | Z% | R% | X%
| CABLE | CABLE | *TOTAL% | CABLE | CABLE | *TOTAL% |  |  | 1000 | 0.0177 | 0.0199 | 0.026438 | [20 empty] | updated 17th Feb. 2000 with table 9 of 5413.7
SIZE | (VOLTS) | ( % ) | FLICKER | (VOLTS) | ( % ) | FLICKER |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C | [6 empty] | LRC VALUES (updated 31dec1997)
2 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | MOTOR SIZES IN HORSE POWER
1 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | SIZE | R@65C | R@90C | X | Z | R@90C | Z | VOLTAGE | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200
1/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 2 | 0.31061 | 0.33653 | 0.045 | 0.28216 | 0.2052 | 0.18366 | 208 | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
2/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 1 | 0.24432 | 0.26471 | 0.046 | 0.22896 | 0.1623 | 0.15215 | 240 | 64 | 85 | 92 | 106 | 127 | 162 | 232 | 290 | 365 | 435 | 580 | 725 | 1085 | 1450 | 2170
3/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.18762 | 0.1334 | 0.12915 | 480 | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
4/0 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.15403 | 0.1028 | 0.10554
250 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.12689 | 0.0825 | 0.089655
350 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.10684 | 0.0653 | 0.076094
500 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.094374 | 0.0552 | 0.068519
750 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075091 | 0.0404 | 0.056758 |  | 3 Phase | Three-Phase Motor (Sized in HP) | [15 empty] | Transformer Data |  | X/R
1000 | 0 | 0 | 3.4093 | 0 | 0 | 0 |  |  | 500 | 0.042235 | 0.04576 | 0.039 | 0.060116 | 0.0289 | 0.047471 |  | Trans | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200 | R | X | Ratio | Z%
[9 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.047969 | 0.0199 | 0.04006 |  | 45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.0191 | 0.0193 | 1.0105 | 2.715%
[9 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.042594 | 0.0157 | 0.036248 |  | 75 | 0.66522 | 0.88072 | 0.95567 | 1.0962 | 1.3117 | 1.6771 | 2.4079 | 3.0076 | 3.7852 | 4.5066 | 6.0057 | 7.5142 | 11.2432 | 15.019 | 22.4864 | 30.0474 | 0.0172 | 0.0151 | 0.87791 | 2.289%
WITH REDUCED LRC TO 770A OR 50HP |  |  |  | *TOTAL FLICKER = CABLE (%) + XMFR (%) | [12 empty] | 150 | 0.3078 | 0.40751 | 0.44219 | 0.54094 | 0.60693 | 0.776 | 1.1141 | 1.3916 | 1.7514 | 2.0852 | 2.7789 | 3.4768 | 5.2022 | 6.9493 | 10.4045 | 13.903 | 0.0114 | 0.0154 | 1.3509 | 1.916%
[10 empty] | 0.023 | 0.024115 |  | 0.077 | 0.080732 |  |  | 225 | 0.20691 | 0.27393 | 0.29724 | 0.34096 | 0.40798 | 0.52163 | 0.74894 | 0.93544 | 1.1773 | 1.4017 | 1.868 | 2.3372 | 3.497 | 4.6714 | 6.994 | 9.3457 | 0.0119 | 0.0154 | 1.2941 | 1.946%
[17 empty] | 300 | 0.19214 | 0.25438 | 0.27603 | 0.31663 | 0.37887 | 0.48441 | 0.69549 | 0.86869 | 1.0933 | 1.3017 | 1.7347 | 2.1704 | 3.2474 | 4.338 | 6.4949 | 8.6788 | 0.0102 | 0.0205 | 2.0098 | 2.29%
Lookup Value |  | 0 | [14 empty] | 500 | 0.22773 | 0.3015 | 0.32716 | 0.37527 | 0.44904 | 0.57413 | 0.82432 | 1.0296 | 1.2958 | 1.5428 | 2.056 | 2.5724 | 3.8489 | 5.1415 | 7.6979 | 10.2863 | 0.0081 | 0.0443 | 5.4691 | 4.503%
Lookup | Wire | Volatge Drop | % Volatge Drop | [13 empty] | 750 | 0.20315 | 0.26896 | 0.29185 | 0.33476 | 0.40057 | 0.51216 | 0.73534 | 0.91846 | 1.1559 | 1.3763 | 1.8341 | 2.2947 | 3.4335 | 4.5866 | 6.867 | 9.176 | 0.0095 | 0.0597 | 6.2842 | 6.045%
1 | 2 | 0 | 0 | [13 empty] | 1000 | 0.14663 | 0.19413 | 0.21065 | 0.24163 | 0.28913 | 0.36968 | 0.53076 | 0.66294 | 0.83435 | 0.99337 | 1.3238 | 1.6563 | 2.4783 | 3.3106 | 4.9565 | 6.6232 | 0.009 | 0.0575 | 6.3889 | 5.82%
2 | 1/0 | 0 | 0 | [13 empty] | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
3 | 3/0 | 0 | 0 | [13 empty] | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
4 | 350 | 0 | 0 | [13 empty] | 2500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
5 | 500 | 0 | 0 | [13 empty] | 3000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
6 | 1000 | 0 | 0 | [13 empty] | Locked Rotor Current
[17 empty] | @208V | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
[17 empty] | @480V | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
1 Phase
Trans
(kVA)
25
50
75
100
[17 empty] | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE |  |  | Three Phase Motor Data |  | Three PH Motor REF | 9 | HP | #N/A
[17 empty] | 1 | 1 |  |  | 1HP | 0.75 | 41.4096 |  |  | LOOKUP | HP | P.F. | REF
[17 empty] | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096 |  |  | 1 | 3 | 0.3 | 11 | SER 1 | 72.5424
[17 empty] | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096 |  |  | 2 | 4.5 | 0.3 | 14 | SER 2 | 72.5424
[17 empty] | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096 |  |  | 3 | 5 | 0.3 | 9 | SER 3 | 72.5424
[17 empty] | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096 |  |  | 4 | 6 | 0.3 |  | SEC 1 | 72.5424
[17 empty] | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096 |  |  | 5 | 7.5 | 0.3 |  |  | 72.5424
[17 empty] | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096 |  |  | 6 | 10 | 0.3 |  |  | 72.5424
[17 empty] | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096 |  |  | 7 | 15 | 0.3 |  |  | 72.5424
[17 empty] | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096 |  |  | 8 | 20 | 0.3 |  |  | 72.5424
[17 empty] | SINGLE PHASE LOOKUPS |  | Single PH Motor REF |  | 5 | HP | #N/A |  |  | 9 | 25 | 0.3 |  |  | 72.5424
[26 empty] | 10 | 30 | 0.3 |  |  | 72.5424
[26 empty] | 11 | 40 | 0.3 |  |  | 72.5424
[26 empty] | 12 | 50 | 0.3 |  |  | 72.5424
[26 empty] | 13 | 60 | 0.3 |  |  | 72.5424
[26 empty] | 14 | 75 | 0.3 |  |  | 72.5424
[26 empty] | 15 | 100 | 0.3 |  |  | 72.5424
[26 empty] | 16 | 150 | 0.3 |  |  | 72.5424
[26 empty] | 17 | 200 | 0.3 |  |  | 72.5424
[26 empty] | 18 | 250 | 0.3 |  |  | 72.5424
[26 empty] | 19 | 300 | 0.3 |  |  | 72.5424
[26 empty] | 20 | 400 | 0.3 |  |  | 72.5424
[26 empty] | 21 | 500 | 0.3 |  |  | 72.5424
[26 empty] | 22 | 600 | 0.3 |  |  | 72.5424
[26 empty] | 23 | 700 | 0.3 |  |  | 72.5424
[26 empty] | 24 | 800 | 0.3 |  |  | 72.5424
[26 empty] | 25 | 900 | 0.3 |  |  | 72.5424
[26 empty] | 26 | 1000 | 0.3 |  |  | 72.5424
[26 empty] | 27 | 1200 | 0.3 |  |  | 72.5424
[26 empty] | 28 | 1500 | 0.3 |  |  | 72.5424

## UGSECVDROP1 (hidden)
[9 empty] | Wire Ref 3PH | 1 | [6 empty] | Ampicity | Check
| Footage | Kw | Transformer | Trans Kw |  |  |  |  | Volt Drop 3ph | 0 |  | CONDUCTOR DATA DESIGN MANUAL |  |  |  |  | 1 PH | OK
Single PH | 0 | 0 | 15 | 0 |  |  |  |  | Wire Ref 1PH | 2 | ALUMINUM CABLES OHMS / 1000 FT |  |  |  | Volt Drop | Amp Check | 3 PH | OK
Array | 0 | 0 | 15 | 0 |  |  |  |  | Volt Drop | 0 | SIZE | R | X | Z |  | 1 through 7 | 7 through 12
Three PH | 0 | 0 | 75 | 0 | [5 empty] | 1 | 2 | 0.267 | 0.0238 | 0.25067 | 0 | OK | NO
UgSerOh | 0 | 0 | [7 empty] | 2 | 1/0 | 0.168 | 0.0241 | 0.1617 | 0 | OK | NO
[9 empty] | 1 | 3 | 3/0 | 0.105 | 0.0226 | 0.10435 | 0 | OK | NO
[9 empty] | 2 | 4 | 350 | 0.0505 | 0.0215 | 0.054822 | 0 | OK | NO
PF | ANGLE |  | 1-PH = 1 | SYSTEM |  | Cable Demand | KW |  | 3 | 5 | 500 | 0.0354 | 0.0207 | 0.040883 | 0 | OK | NO
0.9 | 25.8419 |  | 3-PH = 3 | 1 |  |  | 0 |  | 4 | 6 | 1000 | 0.0177 | 0.0199 | 0.024604 | 0 | OK | NO
VOLTAGE |  |  | RUN |  | FEET |  | L-AMPS |  |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C
120 | 240 |  | 1 |  | 0 |  | 0 |  |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | 600 Volt Secondary Aluminum Cable, DB Conduit (Direct Buried)
|  |  | IF 3 PH | [7 empty] | SIZE | R@65C | R@90C | X | Z | R@90C | Z |  | (With 7-1/2 Inches Centerline to Centerline Spacing Between Conduits)
|  |  | 1 | [7 empty] | 2 | 0.31061 | 0.33653 | 0.045 | 0.32249 | 0.2052 | 0.2043 |  | Cable Size | Conduit | Number of | Number of Runs
[11 empty] | 1 | 0.24432 | 0.26471 | 0.046 | 0.25829 | 0.1623 | 0.16612 |  | Size | Size | Conductors | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Single-Phase Transformers |  |  |  | Three-Phase Transformers | [6 empty] | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.2094 | 0.1334 | 0.13924 |  | 1000 | 5"DB | 3-1/C | 605 | 1104 | 1527 | 1892 | 2335 | 2526 | 2821 | 3080 | 3339 | 3550 | 3707 | 3828
[11 empty] | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.16944 | 0.1028 | 0.11126 |  | 500 | 4"DB | 3-1/C | 397 | 736 | 1029 | 1288 | 1595 | 1746 | 1953 | 2144 | 2313 | 2470 | 2607 | 2712
kVA |  | 15 |  | kVA |  | 75 |  |  |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.13724 | 0.0825 | 0.092557 |  | 350 | 3"DB | 2-1/C | 318 | 600 | 852 | 1076 | 1285 | 1482 | 1673 | 1840 | 2016 | 2160 | 2266 | 2376
Percentage Load |  | 111.1% |  | Percentage Load |  | N/A |  |  |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.11354 | 0.0653 | 0.076641 |  | 350 | 3"DB | 3-1/C | 313 | 586 | 822 | 1036 | 1230 | 1416 | 1589 | 1760 | 1908 | 2040 | 2145 | 2232
%Transformer Volt Drop |  | 2.3 |  | %Transformer Volt Drop |  | 0 |  |  |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.098578 | 0.0552 | 0.067551 |  | 3/0 | 2"DB | 2-1/C | 202 | 386 | 552 | 704 | 875 | 984 | 1113 | 1232 | 1250 | 1440 | 1518 | 1608
Load on Transformer |  | 15 | KW |  |  | 0 | KW |  |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075795 | 0.0404 | 0.053796 |  | 3/0 | 3"DB | 3-1/C | 199 | 376 | 534 | 676 | 810 | 936 | 1057 | 1160 | 1269 | 1350 | 1419 | 1500
[11 empty] | 500 | 0.042235 | 0.04576 | 0.039 | 0.058184 | 0.0289 | 0.04301 |  | 1/0 | 2"DB | 2-1/C | 152 | 292 | 420 | 536 | 645 | 750 | 854 | 944 | 1044 | 1130 | 1188 | 1248
[11 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.043965 | 0.0199 | 0.034474 |  | #2 | 2"DB | 2-1/C | 113 | 218 | 315 | 404 | 490 | 570 | 651 | 720 | 792 | 860 | 913 | 960
[11 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.037873 | 0.0157 | 0.030258 |  | #8 | 1"DB | 1/C | 47 | 92 | 135 | 176 | 215 | 252 | 287 | 320 | 306 | 380 | 407 | 432
Ampacity OK |  | ALUMINUM CABLES |  |  |  | COPPER CABLES
Yes or No | Yes or No |  |  |  | TRANS. + CABLE |  |  | TRANS. + CABLE |  |  |  | 0.023 | 0.024115 |  | 0.077 | 0.080732
1-7 Runs | 8-12 Runs | SIZE | V - DROP | % DROP | %V-DROP | V - DROP | % DROP | V-DROP
OK | NO | 2 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Single Phase Padmount Transformer Size
|  | 1 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [11 empty] | kVA
OK | NO | 1/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Percentage | 15 | 25 | Number of Runs 1: 50; Number of Runs 2: 75; Number of Runs 3: 100; Number of Runs 4: 167; Number of Runs 5: Under 50% Loading
|  | 2/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 50% | 1 | 1 | Number of Runs 1: 1; Number of Runs 2: 0.9; Number of Runs 3: 0.9; Number of Runs 4: 1; Number of Runs 6: #N/A
OK | NO | 3/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 60% | 1.2 | 1.2 | Number of Runs 1: 1.2; Number of Runs 2: 1.1; Number of Runs 3: 1; Number of Runs 4: 1.2; Number of Runs 5: Over 50% Loading
|  | 4/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 70% | 1.5 | 1.4 | Number of Runs 1: 1.4; Number of Runs 2: 1.3; Number of Runs 3: 1.2; Number of Runs 4: 1.4; Number of Runs 6: 2.3
|  | 250 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 50 |  | 80% | 1.7 | 1.6 | Number of Runs 1: 1.6; Number of Runs 2: 1.5; Number of Runs 3: 1.4; Number of Runs 4: 1.6
OK | NO | 350 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 90% | 1.9 | 1.8 | Number of Runs 1: 1.8; Number of Runs 2: 1.6; Number of Runs 3: 1.6; Number of Runs 4: 1.8
OK | NO | 500 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | #VALUE! |  | 100% | 2.1 | 2 | Number of Runs 1: 1.8; Number of Runs 2: 1.8; Number of Runs 3: 1.7; Number of Runs 4: 2
|  | 750 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 60% |  | 110% | 2.3 | 2.2 | Number of Runs 1: 2; Number of Runs 2: 2; Number of Runs 3: 1.9; Number of Runs 4: 2.2
OK | NO | 1000 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 0 |  | 120% | 2.5 | 2.4 | Number of Runs 1: 2.2; Number of Runs 2: 2.2; Number of Runs 3: 2.1; Number of Runs 4: 2.4
[17 empty] | 0 |  | 130% | 2.7 | 2.6 | Number of Runs 1: 2.4; Number of Runs 2: 2.4; Number of Runs 3: 2.3; Number of Runs 4: 2.6
[19 empty] | 140% | 2.9 | 2.8 | Number of Runs 1: 2.6; Number of Runs 2: 2.5; Number of Runs 3: 2.4; Number of Runs 4: 2.9
[17 empty] | 1.35 |  | 150% | 3.1 | 3 | Number of Runs 1: 2.8; Number of Runs 2: 2.7; Number of Runs 3: 2.6; Number of Runs 4: 3.1
[17 empty] | 1 |  | 160% | 3.3 | 3.2 | Number of Runs 1: 2.9; Number of Runs 2: 2.9; Number of Runs 3: 2.8; Number of Runs 4: 3.3
Number of Runs | [16 empty] | 50kVA |  | 170% | 3.5 | 3.4 | Number of Runs 1: 3; Number of Runs 2: 3.1; Number of Runs 3: 3.3; Number of Runs 4: 3.6
1 | [16 empty] | 70%
2 | [16 empty] | #N/A |  | 120/208V Three-Phase Padmount Transformer Size
3 | [18 empty] | Transformer | Kva
4 | [18 empty] | Loading | 45 | 75 | Number of Runs 1: 150; Number of Runs 2: 225; Number of Runs 3: 300; Number of Runs 4: 500; Number of Runs 5: 750; Number of Runs 6: 1000
5 | [18 empty] | 50% | 1.3 | 1.13 | Number of Runs 1: 0.89; Number of Runs 2: 0.91; Number of Runs 3: 0.98; Number of Runs 4: 1.54; Number of Runs 5: 2.03; Number of Runs 6: 1.9
6 | [18 empty] | 60% | 1.6 | 1.35 | Number of Runs 1: 1.07; Number of Runs 2: 1.1; Number of Runs 3: 1.17; Number of Runs 4: 1.8; Number of Runs 5: 2.43; Number of Runs 6: 2.33
7 | [18 empty] | 70% | 1.8 | 1.58 | Number of Runs 1: 1.2; Number of Runs 2: 1.3; Number of Runs 3: 1.37; Number of Runs 4: 2.1; Number of Runs 5: 2.84; Number of Runs 6: 2.72
8 | [18 empty] | 80% | 2.1 | 1.81 | Number of Runs 1: 1.43; Number of Runs 2: 1.46; Number of Runs 3: 1.56; Number of Runs 4: 2.4; Number of Runs 5: 3.2; Number of Runs 6: 3
9 | [18 empty] | 90% | 2.4 | 2.03 | Number of Runs 1: 1.6; Number of Runs 2: 1.64; Number of Runs 3: 1.76; Number of Runs 4: 2.7; Number of Runs 5: 3.6; Number of Runs 6: 3.4
10 | [18 empty] | 100% | 2.6 | 2.26 | Number of Runs 1: 1.78; Number of Runs 2: 1.83; Number of Runs 3: 1.9; Number of Runs 4: 3; Number of Runs 5: 4; Number of Runs 6: 3.8
11 | [18 empty] | 110% | 2.9 | 2.48 | Number of Runs 1: 1.96; Number of Runs 2: 2.01; Number of Runs 3: 2.1; Number of Runs 4: 3.3; Number of Runs 5: 4.3; Number of Runs 6: 4.2
12 | [18 empty] | 120% | 3.2 | 2.71 | Number of Runs 1: 2.14; Number of Runs 2: 2.2; Number of Runs 3: 2.3; Number of Runs 4: 3.6; Number of Runs 5: 4.7; Number of Runs 6: 4.6
[19 empty] | 130% | 3.4 | 2.94 | Number of Runs 1: 2.39; Number of Runs 2: 2.49; Number of Runs 3: 2.72; Number of Runs 4: 4; Number of Runs 5: 5.4; Number of Runs 6: 5.2
[19 empty] | 140% | 3.7 | 3.16 | Number of Runs 1: 2.57; Number of Runs 2: 2.68; Number of Runs 3: 2.93; Number of Runs 4: 4.44; Number of Runs 5: 5.9; Number of Runs 6: 5.6
[19 empty] | 150% | 4 | 3.69 | Number of Runs 1: 2.91; Number of Runs 2: 3.07; Number of Runs 3: 3.37; Number of Runs 4: 5; Number of Runs 5: 6.8; Number of Runs 6: 6.5; Number of Runs 7: Under 50% Loading
#N/A
Over 50% Loading
[19 empty] | 277/480V Three-Phase Padmount Transformer Size |  |  | Number of Runs 8: 0
[19 empty] | Transformer | Kva
[19 empty] | Loading | 75 | 150 | 225 | 300 | 500 | 750 | 1000 | 1500 | 2000 | 2500 | 3000
[19 empty] | 50% | 1.07 | 0.92 | 0.72 | 0.96 | 0.93 | 1.93 | 1.9 | 1.9 | 1.8 | 1.8 | 1.9
[19 empty] | 60% | 1.29 | 1.1 | 0.87 | 1.15 | 1.12 | 2.32 | 2.34 | 2.34 | 2.2 | 2.2 | 2.2
[19 empty] | 70% | 1.5 | 1.3 | 1.01 | 1.3 | 1.3 | 2.6 | 2.73 | 2.6 | 2.63 | 2.6 | 2.6
[19 empty] | 80% | 1.72 | 1.47 | 1.16 | 1.54 | 1.49 | 3 | 3 | 3 | 2.9 | 3.04 | 3
[19 empty] | 90% | 1.93 | 1.65 | 1.3 | 1.73 | 1.68 | 3.4 | 3.4 | 3.4 | 3.3 | 3.3 | 3.3
[19 empty] | 100% | 2.1 | 1.84 | 1.4 | 1.92 | 1.86 | 3.8 | 3.8 | 3.8 | 3.7 | 3.7 | 3.7
[19 empty] | 110% | 2.36 | 2.02 | 1.59 | 2.11 | 2 | 4.1 | 4.2 | 4.2 | 4 | 4.1 | 4.1
[19 empty] | 120% | 2.58 | 2.21 | 1.73 | 2.31 | 2.24 | 4.5 | 4.6 | 4.5 | 4.4 | 4.4 | 4.4
[19 empty] | 130% | 2.79 | 2.5 | 1.88 | 2.6 | 2.5 | 5.2 | 5.2 | 5.3 | 5.1 | 5.2 | 5.2
[19 empty] | 140% | 3.01 | 2.6 | 2.1 | 2.8 | 2.7 | 5.6 | 5.6 | 5.7 | 5.5 | 5.6 | 5.7
[19 empty] | 150% | 3.5 | 3 | 2.4 | 3.3 | 3.1 | 6.4 | 65 | 6.5 | 6.3 | 6.4 | 6.5
2

## UGSECFLCKER1 (hidden)
[39 empty] | 15 | 2.1 | 1.7 | 1.2 | updated 17th Feb. 2000 with table 5 of 5413.7
[39 empty] | 25 | 2 | 1.6 | 1.2
[39 empty] | 50 | 2.1 | 1.3 | 1.7
[39 empty] | 75 | 2 | 1.1 | 1.8 | 1.051 | 1.751
[39 empty] | 100 | 2.2 | 1.1 | 1.9
[22 empty] | LRC VALUES (updated 5 FEB 1998) | [15 empty] | Single Phase kVA | 167 | 2.3 | 1.1 | 2
[23 empty] | SINGLE-PHASE MOTOR SIZES IN HP | [15 empty] | 45 | 2.7153 | 1.91 | 1.93
[22 empty] | VOLTAGE | 1 | 1.5 | 2 | [13 empty] | 75 | 2.2888 | 1.72 | 1.51 | 1.62 | 1.46
[22 empty] | 120 | 46 | 69 | 92 | [13 empty] | 150 | 1.916 | 1.14 | 1.54
[39 empty] | 225 | 1.9462 | 1.19 | 1.54
[16 empty] | CONDUCTOR DATA DESIGN MANUAL | [22 empty] | 300 | 2.2897 | 1.02 | 2.05
PF |  | ANGLE |  | 1-PH = 1 |  | # OF PHASES |  | HP |  | 1Ph-LRC |  | 1Ph-XKMR% |  |  | ALUMINUM CABLES OHMS / 1000 FT | [23 empty] | 500 | 4.5034 | 0.81 | 4.43
0.75 |  | 41.4096 |  | 3-PH = 3 |  | 1 |  | 6 |  | 140 |  | 4.6339 | 1.7 | 1-Ph | SIZE | R | X | Z | L-AMPS |  |  | LRC VALUES (updated 5 FEB 1998) | [16 empty] | 750 | 6.0451 | 0.95 | 5.97
[10 empty] | 3Ph-LRC |  |  | #N/A | 3-Ph | 2 | 0.267 | 0.0238 | 0.21599 | 140 |  |  |  | SINGLE-PHASE MOTOR SIZES IN HORSE POWER | [15 empty] | 1000 | 5.82 | 0.9 | 5.75
[10 empty] | n/a |  |  | X |  | 1/0 | 0.168 | 0.0241 | 0.14194 |  |  |  | VOLTAGE | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 10 | [7 empty] | 1500 | 0 | 0 | 0
VOLTAGE |  |  |  | RUN |  | FEET |  | KW |  | XFMR KVA |  | 3Ph-XFMR % | 1.2 | 1-Ph | 3/0 | 0.105 | 0.0226 | 0.093698 |  |  |  | 240 | 27 | 34 | 46 | 69 | 103 | 115 | 140 | 175 | 218 | [7 empty] | 2000 | 0 | 0 | 0
120 |  | 240 |  | 1 |  | 0 |  | 25.2 |  | 15 |  | 0 | #N/A |  | 350 | 0.0505 | 0.0215 | 0.052096 | [20 empty] | 2500 | 0 | 0 | 0
[15 empty] | 500 | 0.0354 | 0.0207 | 0.040242 | [20 empty] | 3000 | 0 | 0 | 0
ALUMINUM CABLES | [7 empty] | COPPER CABLES | [29 empty] | Three Phase kVA | Three Phase kVA | Z% | R% | X%
|  | CABLE |  | CABLE |  | *TOTAL% |  | CABLE |  | CABLE |  | *TOTAL% |  |  | 1000 | 0.0177 | 0.0199 | 0.026438 | [20 empty] | updated 17th Feb. 2000 with table 9 of 5413.7
SIZE |  | (VOLTS) |  | ( % ) |  | FLICKER |  | (VOLTS) |  | ( % ) |  | FLICKER |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C | [6 empty] | LRC VALUES (updated 31dec1997)
2 |  | 0 |  | 0 |  | 4.6339 |  | 0 |  | 0 |  | 0 |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | MOTOR SIZES IN HORSE POWER
1 |  | 0 |  | 0 |  | 4.6339 |  | 0 |  | 0 |  | 0 |  |  | SIZE | R@65C | R@90C | X | Z | R@90C | Z | VOLTAGE | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200
1/0 |  | 0 |  | 0 |  | 4.6339 |  | 0 |  | 0 |  | 0 |  |  | 2 | 0.31061 | 0.33653 | 0.045 | 0.28216 | 0.2052 | 0.18366 | 208 | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
2/0 |  | 0 |  | 0 |  | 4.6339 |  | 0 |  | 0 |  | 0 |  |  | 1 | 0.24432 | 0.26471 | 0.046 | 0.22896 | 0.1623 | 0.15215 | 240 | 64 | 85 | 92 | 106 | 127 | 162 | 232 | 290 | 365 | 435 | 580 | 725 | 1085 | 1450 | 2170
3/0 |  | 0 |  | 0 |  | 4.6339 |  | 0 |  | 0 |  | 0 |  |  | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.18762 | 0.1334 | 0.12915 | 480 | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
4/0 |  | 0 |  | 0 |  | 4.6339 |  | 0 |  | 0 |  | 0 |  |  | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.15403 | 0.1028 | 0.10554
250 |  | 0 |  | 0 |  | 4.6339 |  | 0 |  | 0 |  | 0 |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.12689 | 0.0825 | 0.089655
350 |  | 0 |  | 0 |  | 4.6339 |  | 0 |  | 0 |  | 0 |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.10684 | 0.0653 | 0.076094
500 |  | 0 |  | 0 |  | 4.6339 |  | 0 |  | 0 |  | 0 |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.094374 | 0.0552 | 0.068519
750 |  | 0 |  | 0 |  | 4.6339 |  | 0 |  | 0 |  | 0 |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075091 | 0.0404 | 0.056758 |  | 3 Phase | Three-Phase Motor (Sized in HP) | [15 empty] | Transformer Data |  | X/R
1000 |  | 0 |  | 0 |  | 4.6339 |  | 0 |  | 0 |  | 0 |  |  | 500 | 0.042235 | 0.04576 | 0.039 | 0.060116 | 0.0289 | 0.047471 |  | Trans | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200 | R | X | Ratio | Z%
[15 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.047969 | 0.0199 | 0.04006 |  | 45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.0191 | 0.0193 | 1.0105 | 2.715%
[15 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.042594 | 0.0157 | 0.036248 |  | 75 | 0.66522 | 0.88072 | 0.95567 | 1.0962 | 1.3117 | 1.6771 | 2.4079 | 3.0076 | 3.7852 | 4.5066 | 6.0057 | 7.5142 | 11.2432 | 15.019 | 22.4864 | 30.0474 | 0.0172 | 0.0151 | 0.87791 | 2.289%
WITH REDUCED LRC TO 770A OR 50HP | [7 empty] | *TOTAL FLICKER = CABLE (%) + XMFR (%) | [14 empty] | 150 | 0.3078 | 0.40751 | 0.44219 | 0.54094 | 0.60693 | 0.776 | 1.1141 | 1.3916 | 1.7514 | 2.0852 | 2.7789 | 3.4768 | 5.2022 | 6.9493 | 10.4045 | 13.903 | 0.0114 | 0.0154 | 1.3509 | 1.916%
[16 empty] | 0.023 | 0.024115 |  | 0.077 | 0.080732 |  |  | 225 | 0.20691 | 0.27393 | 0.29724 | 0.34096 | 0.40798 | 0.52163 | 0.74894 | 0.93544 | 1.1773 | 1.4017 | 1.868 | 2.3372 | 3.497 | 4.6714 | 6.994 | 9.3457 | 0.0119 | 0.0154 | 1.2941 | 1.946%
[23 empty] | 300 | 0.19214 | 0.25438 | 0.27603 | 0.31663 | 0.37887 | 0.48441 | 0.69549 | 0.86869 | 1.0933 | 1.3017 | 1.7347 | 2.1704 | 3.2474 | 4.338 | 6.4949 | 8.6788 | 0.0102 | 0.0205 | 2.0098 | 2.29%
Lookup Value |  |  | 1ph | 0 | 3ph | 0 | SER 4 | SER9 | SER5 |  | SER 10 | SER 2 |  |  | SER 1 | [7 empty] | 500 | 0.22773 | 0.3015 | 0.32716 | 0.37527 | 0.44904 | 0.57413 | 0.82432 | 1.0296 | 1.2958 | 1.5428 | 2.056 | 2.5724 | 3.8489 | 5.1415 | 7.6979 | 10.2863 | 0.0081 | 0.0443 | 5.4691 | 4.503%
Lookup |  | Wire |  | Volatge Drop |  | % Volatge Drop |  | Z |  | X% | [12 empty] | 750 | 0.20315 | 0.26896 | 0.29185 | 0.33476 | 0.40057 | 0.51216 | 0.73534 | 0.91846 | 1.1559 | 1.3763 | 1.8341 | 2.2947 | 3.4335 | 4.5866 | 6.867 | 9.176 | 0.0095 | 0.0597 | 6.2842 | 6.045%
1 |  | 2 |  | 0 |  | 0 | 0.28216 | 0.28216 | 0.28216 | 0.045 | 0.28216 | 0.28216 | 0 | SER 4 | 0.28216 | [7 empty] | 1000 | 0.14663 | 0.19413 | 0.21065 | 0.24163 | 0.28913 | 0.36968 | 0.53076 | 0.66294 | 0.83435 | 0.99337 | 1.3238 | 1.6563 | 2.4783 | 3.3106 | 4.9565 | 6.6232 | 0.009 | 0.0575 | 6.3889 | 5.82%
2 |  | 1/0 |  | 0 |  | 0 | 0.18762 | 0.18762 | 0.18762 | 0.044 | 0.18762 | 0.18762 | 0 | SER 9 | 0.18762 | [7 empty] | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
3 | 1 | 3/0 |  | 0 |  | 0 | 0.12689 | 0.12689 | 0.12689 | 0.042 | 0.12689 | 0.12689 | 0 | SER5 | 0.12689 | [7 empty] | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
4 | 2 | 350 |  | 0 |  | 0 | 0.075091 | 0.075091 | 0.075091 | 0.04 | 0.075091 | 0.075091 | 0 | SER10 | 0.075091 | [7 empty] | 2500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
5 | 3 | 500 |  | 0 |  | 0 | 0.060116 | 0.060116 | 0.060116 | 0.039 | 0.060116 | 0.060116 | 0 | SER 2 | 0.060116 | [7 empty] | 3000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
6 | 4 | 1000 |  | 0 |  | 0 | [6 empty] | 0 | SER.1 | [8 empty] | Locked Rotor Current
[23 empty] | @208V | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
[23 empty] | @480V | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
1 Phase
Trans
(kVA)
25
50
75
100
[23 empty] | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE |  |  | Three Phase Motor Data |  | Three PH Motor REF | 1 | HP | #N/A
[23 empty] | 1 | 1 |  |  | 1HP | 0.75 | 41.4096 |  |  | LOOKUP | HP | P.F. | REF
[23 empty] | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096 |  |  | 1 | 3 | 0.3 | 11 | SER 1 | 72.5424
[23 empty] | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096 |  |  | 2 | 4.5 | 0.3 | 14 | SER 2 | 72.5424
[23 empty] | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096 |  |  | 3 | 5 | 0.3 | 9 | SER 3 | 72.5424
[23 empty] | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096 |  |  | 4 | 6 | 0.3 |  | SEC 1 | 72.5424
[23 empty] | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096 |  |  | 5 | 7.5 | 0.3 |  |  | 72.5424
[23 empty] | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096 |  |  | 6 | 10 | 0.3 |  |  | 72.5424
[23 empty] | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096 |  |  | 7 | 15 | 0.3 |  |  | 72.5424
[23 empty] | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096 |  |  | 8 | 20 | 0.3 |  |  | 72.5424
[23 empty] | SINGLE PHASE LOOKUPS |  | Single PH Motor REF |  | 7 | HP | #N/A |  |  | 9 | 25 | 0.3 |  |  | 72.5424
[32 empty] | 10 | 30 | 0.3 |  |  | 72.5424
[32 empty] | 11 | 40 | 0.3 |  |  | 72.5424
[32 empty] | 12 | 50 | 0.3 |  |  | 72.5424
[32 empty] | 13 | 75 | 0.3 |  |  | 72.5424
[32 empty] | 14 | 100 | 0.3 |  |  | 72.5424
[32 empty] | 15 | 150 | 0.3 |  |  | 72.5424
[32 empty] | 16 | 200 | 0.3 |  |  | 72.5424
[32 empty] | 17 | 250 | 0.3 |  |  | 72.5424
[32 empty] | 18 | 300 | 0.3 |  |  | 72.5424
[32 empty] | 19 | 400 | 0.3 |  |  | 72.5424
[32 empty] | 20 | 500 | 0.3 |  |  | 72.5424
[32 empty] | 21 | 600 | 0.3 |  |  | 72.5424
[32 empty] | 22 | 700 | 0.3 |  |  | 72.5424
[32 empty] | 23 | 800 | 0.3 |  |  | 72.5424
[32 empty] | 24 | 900 | 0.3 |  |  | 72.5424
[32 empty] | 25 | 1000 | 0.3 |  |  | 72.5424
[32 empty] | 26 | 1200 | 0.3 |  |  | 72.5424
[32 empty] | 27 | 1500 | 0.3 |  |  | 72.5424
[32 empty] | 28 | 1500 | 0.3 |  |  | 72.5424

## UGSECVDROP2 (hidden)
[17 empty] | Ampicity | Check
Transformer | Trans Kw | [10 empty] | CONDUCTOR DATA DESIGN MANUAL |  |  |  |  | 1 PH | OK
15 | #REF! | [7 empty] | Wire Ref | 2 | ALUMINUM CABLES OHMS / 1000 FT |  |  |  | Volt Drop | Amp Check | 3 PH | #N/A
15 | 0 | [7 empty] | Volt Drop | 0 | SIZE | R | X | Z |  | 1 through 7 | 7 through 12
75 | 0 | [8 empty] | 1 | 2 | 0.267 | 0.0238 | 0.25067 | 0 | OK | NO
[10 empty] | 2 | 1/0 | 0.168 | 0.0241 | 0.1617 | 0 | OK | NO
[9 empty] | 1 | 3 | 3/0 | 0.105 | 0.0226 | 0.10435 | 0 | OK | NO
[9 empty] | 2 | 4 | 350 | 0.0505 | 0.0215 | 0.054822 | 0 | OK | NO
PF | ANGLE |  | 1-PH = 1 | SYSTEM |  | Cable Demand | KW |  | 3 | 5 | 500 | 0.0354 | 0.0207 | 0.040883 | 0 | OK | NO
0.9 | 25.8419 |  | 3-PH = 3 | 1 |  |  | 0 |  | 4 | 6 | 1000 | 0.0177 | 0.0199 | 0.024604 | 0 | OK | NO
VOLTAGE |  |  | RUN |  | FEET |  | L-AMPS |  |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C
120 | 240 |  | 1 |  | 0 |  | 0 |  |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | 600 Volt Secondary Aluminum Cable, DB Conduit (Direct Buried)
|  |  | IF 3 PH | [7 empty] | SIZE | R@65C | R@90C | X | Z | R@90C | Z |  | (With 7-1/2 Inches Centerline to Centerline Spacing Between Conduits)
|  |  | 1 | [7 empty] | 2 | 0.31061 | 0.33653 | 0.045 | 0.32249 | 0.2052 | 0.2043 |  | Cable Size | Conduit | Number of | Number of Runs
[11 empty] | 1 | 0.24432 | 0.26471 | 0.046 | 0.25829 | 0.1623 | 0.16612 |  | Size | Size | Conductors | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Single-Phase Transformers |  |  |  | Three-Phase Transformers | [6 empty] | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.2094 | 0.1334 | 0.13924 |  | 1000 | 5"DB | 3-1/C | 605 | 1104 | 1527 | 1892 | 2335 | 2526 | 2821 | 3080 | 3339 | 3550 | 3707 | 3828
[11 empty] | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.16944 | 0.1028 | 0.11126 |  | 500 | 4"DB | 3-1/C | 397 | 736 | 1029 | 1288 | 1595 | 1746 | 1953 | 2144 | 2313 | 2470 | 2607 | 2712
kVA |  | 15 |  | kVA |  | 75 |  |  |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.13724 | 0.0825 | 0.092557 |  | 350 | 3"DB | 2-1/C | 318 | 600 | 852 | 1076 | 1285 | 1482 | 1673 | 1840 | 2016 | 2160 | 2266 | 2376
Percentage Load |  | 111.1% |  | Percentage Load |  | N/A |  |  |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.11354 | 0.0653 | 0.076641 |  | 350 | 3"DB | 3-1/C | 313 | 586 | 822 | 1036 | 1230 | 1416 | 1589 | 1760 | 1908 | 2040 | 2145 | 2232
%Transformer Volt Drop |  | 2.3 |  | %Transformer Volt Drop |  | 0 |  |  |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.098578 | 0.0552 | 0.067551 |  | 3/0 | 2"DB | 2-1/C | 202 | 386 | 552 | 704 | 875 | 984 | 1113 | 1232 | 1250 | 1440 | 1518 | 1608
Load on Transformer |  | 15 | KW |  |  | 0 | KW |  |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075795 | 0.0404 | 0.053796 |  | 3/0 | 3"DB | 3-1/C | 199 | 376 | 534 | 676 | 810 | 936 | 1057 | 1160 | 1269 | 1350 | 1419 | 1500
[11 empty] | 500 | 0.042235 | 0.04576 | 0.039 | 0.058184 | 0.0289 | 0.04301 |  | 1/0 | 2"DB | 2-1/C | 152 | 292 | 420 | 536 | 645 | 750 | 854 | 944 | 1044 | 1130 | 1188 | 1248
[11 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.043965 | 0.0199 | 0.034474 |  | #2 | 2"DB | 2-1/C | 113 | 218 | 315 | 404 | 490 | 570 | 651 | 720 | 792 | 860 | 913 | 960
[11 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.037873 | 0.0157 | 0.030258 |  | #8 | 1"DB | 1/C | 47 | 92 | 135 | 176 | 215 | 252 | 287 | 320 | 306 | 380 | 407 | 432
Ampacity OK |  | ALUMINUM CABLES |  |  |  | COPPER CABLES
Yes or No | Yes or No |  |  |  | TRANS. + CABLE |  |  | TRANS. + CABLE |  |  |  | 0.023 | 0.024115 |  | 0.077 | 0.080732
1-7 Runs | 8-12 Runs | SIZE | V - DROP | % DROP | %V-DROP | V - DROP | % DROP | V-DROP
OK | NO | 2 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Single Phase Padmount Transformer Size
|  | 1 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [11 empty] | kVA
OK | NO | 1/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Percentage | 15 | 25 | Number of Runs 1: 50; Number of Runs 2: 75; Number of Runs 3: 100; Number of Runs 4: 167; Number of Runs 5: Under 50% Loading
|  | 2/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 50% | 1 | 1 | Number of Runs 1: 1; Number of Runs 2: 0.9; Number of Runs 3: 0.9; Number of Runs 4: 1; Number of Runs 6: #N/A
OK | NO | 3/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 60% | 1.2 | 1.2 | Number of Runs 1: 1.2; Number of Runs 2: 1.1; Number of Runs 3: 1; Number of Runs 4: 1.2; Number of Runs 5: Over 50% Loading
|  | 4/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 70% | 1.5 | 1.4 | Number of Runs 1: 1.4; Number of Runs 2: 1.3; Number of Runs 3: 1.2; Number of Runs 4: 1.4; Number of Runs 6: 2.3
|  | 250 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 50 |  | 80% | 1.7 | 1.6 | Number of Runs 1: 1.6; Number of Runs 2: 1.5; Number of Runs 3: 1.4; Number of Runs 4: 1.6
OK | NO | 350 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 90% | 1.9 | 1.8 | Number of Runs 1: 1.8; Number of Runs 2: 1.6; Number of Runs 3: 1.6; Number of Runs 4: 1.8
OK | NO | 500 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | #VALUE! |  | 100% | 2.1 | 2 | Number of Runs 1: 1.8; Number of Runs 2: 1.8; Number of Runs 3: 1.7; Number of Runs 4: 2
|  | 750 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 60% |  | 110% | 2.3 | 2.2 | Number of Runs 1: 2; Number of Runs 2: 2; Number of Runs 3: 1.9; Number of Runs 4: 2.2
OK | NO | 1000 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 0 |  | 120% | 2.5 | 2.4 | Number of Runs 1: 2.2; Number of Runs 2: 2.2; Number of Runs 3: 2.1; Number of Runs 4: 2.4
[17 empty] | 0 |  | 130% | 2.7 | 2.6 | Number of Runs 1: 2.4; Number of Runs 2: 2.4; Number of Runs 3: 2.3; Number of Runs 4: 2.6
[19 empty] | 140% | 2.9 | 2.8 | Number of Runs 1: 2.6; Number of Runs 2: 2.5; Number of Runs 3: 2.4; Number of Runs 4: 2.9
[17 empty] | 1.35 |  | 150% | 3.1 | 3 | Number of Runs 1: 2.8; Number of Runs 2: 2.7; Number of Runs 3: 2.6; Number of Runs 4: 3.1
[17 empty] | 1 |  | 160% | 3.3 | 3.2 | Number of Runs 1: 2.9; Number of Runs 2: 2.9; Number of Runs 3: 2.8; Number of Runs 4: 3.3
[17 empty] | 50kVA |  | 170% | 3.5 | 3.4 | Number of Runs 1: 3; Number of Runs 2: 3.1; Number of Runs 3: 3.3; Number of Runs 4: 3.6
70%
[17 empty] | #N/A |  | 120/208V Three-Phase Padmount Transformer Size
[19 empty] | Transformer | Kva
[19 empty] | Loading | 45 | 75 | Number of Runs 1: 150; Number of Runs 2: 225; Number of Runs 3: 300; Number of Runs 4: 500; Number of Runs 5: 750; Number of Runs 6: 1000
[19 empty] | 50% | 1.3 | 1.13 | Number of Runs 1: 0.89; Number of Runs 2: 0.91; Number of Runs 3: 0.98; Number of Runs 4: 1.54; Number of Runs 5: 2.03; Number of Runs 6: 1.9
[19 empty] | 60% | 1.6 | 1.35 | Number of Runs 1: 1.07; Number of Runs 2: 1.1; Number of Runs 3: 1.17; Number of Runs 4: 1.8; Number of Runs 5: 2.43; Number of Runs 6: 2.33
[19 empty] | 70% | 1.8 | 1.58 | Number of Runs 1: 1.2; Number of Runs 2: 1.3; Number of Runs 3: 1.37; Number of Runs 4: 2.1; Number of Runs 5: 2.84; Number of Runs 6: 2.72
[19 empty] | 80% | 2.1 | 1.81 | Number of Runs 1: 1.43; Number of Runs 2: 1.46; Number of Runs 3: 1.56; Number of Runs 4: 2.4; Number of Runs 5: 3.2; Number of Runs 6: 3
[19 empty] | 90% | 2.4 | 2.03 | Number of Runs 1: 1.6; Number of Runs 2: 1.64; Number of Runs 3: 1.76; Number of Runs 4: 2.7; Number of Runs 5: 3.6; Number of Runs 6: 3.4
[19 empty] | 100% | 2.6 | 2.26 | Number of Runs 1: 1.78; Number of Runs 2: 1.83; Number of Runs 3: 1.9; Number of Runs 4: 3; Number of Runs 5: 4; Number of Runs 6: 3.8
[19 empty] | 110% | 2.9 | 2.48 | Number of Runs 1: 1.96; Number of Runs 2: 2.01; Number of Runs 3: 2.1; Number of Runs 4: 3.3; Number of Runs 5: 4.3; Number of Runs 6: 4.2
[19 empty] | 120% | 3.2 | 2.71 | Number of Runs 1: 2.14; Number of Runs 2: 2.2; Number of Runs 3: 2.3; Number of Runs 4: 3.6; Number of Runs 5: 4.7; Number of Runs 6: 4.6
[19 empty] | 130% | 3.4 | 2.94 | Number of Runs 1: 2.39; Number of Runs 2: 2.49; Number of Runs 3: 2.72; Number of Runs 4: 4; Number of Runs 5: 5.4; Number of Runs 6: 5.2
[19 empty] | 140% | 3.7 | 3.16 | Number of Runs 1: 2.57; Number of Runs 2: 2.68; Number of Runs 3: 2.93; Number of Runs 4: 4.44; Number of Runs 5: 5.9; Number of Runs 6: 5.6
[19 empty] | 150% | 4 | 3.69 | Number of Runs 1: 2.91; Number of Runs 2: 3.07; Number of Runs 3: 3.37; Number of Runs 4: 5; Number of Runs 5: 6.8; Number of Runs 6: 6.5; Number of Runs 7: Under 50% Loading
#N/A
Over 50% Loading
[19 empty] | 277/480V Three-Phase Padmount Transformer Size |  |  | Number of Runs 8: 0
[19 empty] | Transformer | Kva
[19 empty] | Loading | 75 | 150 | 225 | 300 | 500 | 750 | 1000 | 1500 | 2000 | 2500 | 3000
[19 empty] | 50% | 1.07 | 0.92 | 0.72 | 0.96 | 0.93 | 1.93 | 1.9 | 1.9 | 1.8 | 1.8 | 1.9
[19 empty] | 60% | 1.29 | 1.1 | 0.87 | 1.15 | 1.12 | 2.32 | 2.34 | 2.34 | 2.2 | 2.2 | 2.2
[19 empty] | 70% | 1.5 | 1.3 | 1.01 | 1.3 | 1.3 | 2.6 | 2.73 | 2.6 | 2.63 | 2.6 | 2.6
[19 empty] | 80% | 1.72 | 1.47 | 1.16 | 1.54 | 1.49 | 3 | 3 | 3 | 2.9 | 3.04 | 3
[19 empty] | 90% | 1.93 | 1.65 | 1.3 | 1.73 | 1.68 | 3.4 | 3.4 | 3.4 | 3.3 | 3.3 | 3.3
[19 empty] | 100% | 2.1 | 1.84 | 1.4 | 1.92 | 1.86 | 3.8 | 3.8 | 3.8 | 3.7 | 3.7 | 3.7
[19 empty] | 110% | 2.36 | 2.02 | 1.59 | 2.11 | 2 | 4.1 | 4.2 | 4.2 | 4 | 4.1 | 4.1
[19 empty] | 120% | 2.58 | 2.21 | 1.73 | 2.31 | 2.24 | 4.5 | 4.6 | 4.5 | 4.4 | 4.4 | 4.4
[19 empty] | 130% | 2.79 | 2.5 | 1.88 | 2.6 | 2.5 | 5.2 | 5.2 | 5.3 | 5.1 | 5.2 | 5.2
[19 empty] | 140% | 3.01 | 2.6 | 2.1 | 2.8 | 2.7 | 5.6 | 5.6 | 5.7 | 5.5 | 5.6 | 5.7
[19 empty] | 150% | 3.5 | 3 | 2.4 | 3.3 | 3.1 | 6.4 | 65 | 6.5 | 6.3 | 6.4 | 6.5
2

## UGSECFLCKER2 (hidden)
[35 empty] | 15 | 2.1 | 1.7 | 1.2 | updated 17th Feb. 2000 with table 5 of 5413.7
[35 empty] | 25 | 2 | 1.6 | 1.2
[35 empty] | 50 | 2.1 | 1.3 | 1.7
[35 empty] | 75 | 2 | 1.1 | 1.8 | 1.051 | 1.751
[35 empty] | 100 | 2.2 | 1.1 | 1.9
[18 empty] | LRC VALUES (updated 5 FEB 1998) | [15 empty] | Single Phase kVA | 167 | 2.3 | 1.1 | 2
[19 empty] | SINGLE-PHASE MOTOR SIZES IN HP | [15 empty] | 45 | 2.7153 | 1.91 | 1.93
[18 empty] | VOLTAGE | 1 | 1.5 | 2 | [13 empty] | 75 | 2.2888 | 1.72 | 1.51 | 1.62 | 1.46
[18 empty] | 120 | 46 | 69 | 92 | [13 empty] | 150 | 1.916 | 1.14 | 1.54
[35 empty] | 225 | 1.9462 | 1.19 | 1.54
[12 empty] | CONDUCTOR DATA DESIGN MANUAL | [22 empty] | 300 | 2.2897 | 1.02 | 2.05
PF | ANGLE | 1-PH = 1 | # OF PHASES | HP |  | 1Ph-LRC |  | 1Ph-XKMR% |  |  | ALUMINUM CABLES OHMS / 1000 FT | [23 empty] | 500 | 4.5034 | 0.81 | 4.43
0.75 | 41.4096 | 3-PH = 3 | 1 | 7.5 |  | 175 |  | 5.7924 | 1.7 | 1-Ph | SIZE | R | X | Z | L-AMPS |  |  | LRC VALUES (updated 5 FEB 1998) | [16 empty] | 750 | 6.0451 | 0.95 | 5.97
[6 empty] | 3Ph-LRC |  |  | #N/A | 3-Ph | 2 | 0.267 | 0.0238 | 0.21599 | 175 |  |  |  | SINGLE-PHASE MOTOR SIZES IN HORSE POWER | [15 empty] | 1000 | 5.82 | 0.9 | 5.75
[6 empty] | n/a |  |  | X |  | 1/0 | 0.168 | 0.0241 | 0.14194 |  |  |  | VOLTAGE | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 10 | [7 empty] | 1500 | 0 | 0 | 0
VOLTAGE |  | RUN | FEET | KW |  | XFMR KVA |  | 3Ph-XFMR % | 1.2 | 1-Ph | 3/0 | 0.105 | 0.0226 | 0.093698 |  |  |  | 240 | 27 | 34 | 46 | 69 | 103 | 115 | 140 | 175 | 218 | [7 empty] | 2000 | 0 | 0 | 0
120 | 240 | 1 | 0 | 31.5 |  | 15 |  | 0 | #N/A |  | 350 | 0.0505 | 0.0215 | 0.052096 | [20 empty] | 2500 | 0 | 0 | 0
[11 empty] | 500 | 0.0354 | 0.0207 | 0.040242 | [20 empty] | 3000 | 0 | 0 | 0
ALUMINUM CABLES |  |  |  | COPPER CABLES | [29 empty] | Three Phase kVA | Three Phase kVA | Z% | R% | X%
| CABLE | CABLE | *TOTAL% | CABLE |  | CABLE |  | *TOTAL% |  |  | 1000 | 0.0177 | 0.0199 | 0.026438 | [20 empty] | updated 17th Feb. 2000 with table 9 of 5413.7
SIZE | (VOLTS) | ( % ) | FLICKER | (VOLTS) |  | ( % ) |  | FLICKER |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C | [6 empty] | LRC VALUES (updated 31dec1997)
2 | 0 | 0 | 5.7924 | 0 |  | 0 |  | 0 |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | MOTOR SIZES IN HORSE POWER
1 | 0 | 0 | 5.7924 | 0 |  | 0 |  | 0 |  |  | SIZE | R@65C | R@90C | X | Z | R@90C | Z | VOLTAGE | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200
1/0 | 0 | 0 | 5.7924 | 0 |  | 0 |  | 0 |  |  | 2 | 0.31061 | 0.33653 | 0.045 | 0.28216 | 0.2052 | 0.18366 | 208 | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
2/0 | 0 | 0 | 5.7924 | 0 |  | 0 |  | 0 |  |  | 1 | 0.24432 | 0.26471 | 0.046 | 0.22896 | 0.1623 | 0.15215 | 240 | 64 | 85 | 92 | 106 | 127 | 162 | 232 | 290 | 365 | 435 | 580 | 725 | 1085 | 1450 | 2170
3/0 | 0 | 0 | 5.7924 | 0 |  | 0 |  | 0 |  |  | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.18762 | 0.1334 | 0.12915 | 480 | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
4/0 | 0 | 0 | 5.7924 | 0 |  | 0 |  | 0 |  |  | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.15403 | 0.1028 | 0.10554
250 | 0 | 0 | 5.7924 | 0 |  | 0 |  | 0 |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.12689 | 0.0825 | 0.089655
350 | 0 | 0 | 5.7924 | 0 |  | 0 |  | 0 |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.10684 | 0.0653 | 0.076094
500 | 0 | 0 | 5.7924 | 0 |  | 0 |  | 0 |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.094374 | 0.0552 | 0.068519
750 | 0 | 0 | 5.7924 | 0 |  | 0 |  | 0 |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075091 | 0.0404 | 0.056758 |  | 3 Phase | Three-Phase Motor (Sized in HP) | [15 empty] | Transformer Data |  | X/R
1000 | 0 | 0 | 5.7924 | 0 |  | 0 |  | 0 |  |  | 500 | 0.042235 | 0.04576 | 0.039 | 0.060116 | 0.0289 | 0.047471 |  | Trans | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200 | R | X | Ratio | Z%
[11 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.047969 | 0.0199 | 0.04006 |  | 45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.0191 | 0.0193 | 1.0105 | 2.715%
[11 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.042594 | 0.0157 | 0.036248 |  | 75 | 0.66522 | 0.88072 | 0.95567 | 1.0962 | 1.3117 | 1.6771 | 2.4079 | 3.0076 | 3.7852 | 4.5066 | 6.0057 | 7.5142 | 11.2432 | 15.019 | 22.4864 | 30.0474 | 0.0172 | 0.0151 | 0.87791 | 2.289%
WITH REDUCED LRC TO 770A OR 50HP |  |  |  | *TOTAL FLICKER = CABLE (%) + XMFR (%) | [14 empty] | 150 | 0.3078 | 0.40751 | 0.44219 | 0.54094 | 0.60693 | 0.776 | 1.1141 | 1.3916 | 1.7514 | 2.0852 | 2.7789 | 3.4768 | 5.2022 | 6.9493 | 10.4045 | 13.903 | 0.0114 | 0.0154 | 1.3509 | 1.916%
[12 empty] | 0.023 | 0.024115 |  | 0.077 | 0.080732 |  |  | 225 | 0.20691 | 0.27393 | 0.29724 | 0.34096 | 0.40798 | 0.52163 | 0.74894 | 0.93544 | 1.1773 | 1.4017 | 1.868 | 2.3372 | 3.497 | 4.6714 | 6.994 | 9.3457 | 0.0119 | 0.0154 | 1.2941 | 1.946%
[19 empty] | 300 | 0.19214 | 0.25438 | 0.27603 | 0.31663 | 0.37887 | 0.48441 | 0.69549 | 0.86869 | 1.0933 | 1.3017 | 1.7347 | 2.1704 | 3.2474 | 4.338 | 6.4949 | 8.6788 | 0.0102 | 0.0205 | 2.0098 | 2.29%
Lookup Value |  | 0 | [16 empty] | 500 | 0.22773 | 0.3015 | 0.32716 | 0.37527 | 0.44904 | 0.57413 | 0.82432 | 1.0296 | 1.2958 | 1.5428 | 2.056 | 2.5724 | 3.8489 | 5.1415 | 7.6979 | 10.2863 | 0.0081 | 0.0443 | 5.4691 | 4.503%
Lookup | Wire | Volatge Drop | % Volatge Drop | SER 2 | SER 7 | X% | SER 1 | SER 6 | [10 empty] | 750 | 0.20315 | 0.26896 | 0.29185 | 0.33476 | 0.40057 | 0.51216 | 0.73534 | 0.91846 | 1.1559 | 1.3763 | 1.8341 | 2.2947 | 3.4335 | 4.5866 | 6.867 | 9.176 | 0.0095 | 0.0597 | 6.2842 | 6.045%
1 | 2 | 0 | 0 | 0.28216 | 0.28216 | 0.045 | 0.28216 | 0.28216 | 0 | SER 2 | [8 empty] | 1000 | 0.14663 | 0.19413 | 0.21065 | 0.24163 | 0.28913 | 0.36968 | 0.53076 | 0.66294 | 0.83435 | 0.99337 | 1.3238 | 1.6563 | 2.4783 | 3.3106 | 4.9565 | 6.6232 | 0.009 | 0.0575 | 6.3889 | 5.82%
2 | 1/0 | 0 | 0 | 0.18762 | 0.18762 | 0.044 | 0.18762 | 0.18762 | 0 | SER 7 | [8 empty] | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
3 | 3/0 | 0 | 0 | 0.12689 | 0.12689 | 0.042 | 0.12689 | 0.12689 | 0 | SER 1 | [8 empty] | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
4 | 350 | 0 | 0 | 0.075091 | 0.075091 | 0.04 | 0.075091 | 0.075091 | 0 | SER 6 | [8 empty] | 2500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
5 | 500 | 0 | 0 | 0.060116 | 0.060116 | 0.039 | 0.060116 | 0.060116 | [10 empty] | 3000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
6 | 1000 | 0 | 0 | [15 empty] | Locked Rotor Current
[19 empty] | @208V | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
[19 empty] | @480V | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
1 Phase
Trans
(kVA)
25
50
75
100
[19 empty] | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE |  |  | Three Phase Motor Data |  | Three PH Motor REF | 9 | HP | #N/A
[19 empty] | 1 | 1 |  |  | 1HP | 0.75 | 41.4096 |  |  | LOOKUP | HP | P.F. | REF
[19 empty] | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096 |  |  | 1 | 3 | 0.3 | 11 | SER 1 | 72.5424
[19 empty] | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096 |  |  | 2 | 4.5 | 0.3 | 14 | SER 2 | 72.5424
[19 empty] | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096 |  |  | 3 | 5 | 0.3 | 9 | SER 3 | 72.5424
[19 empty] | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096 |  |  | 4 | 6 | 0.3 |  | SEC 1 | 72.5424
[19 empty] | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096 |  |  | 5 | 7.5 | 0.3 |  |  | 72.5424
[19 empty] | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096 |  |  | 6 | 10 | 0.3 |  |  | 72.5424
[19 empty] | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096 |  |  | 7 | 15 | 0.3 |  |  | 72.5424
[19 empty] | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096 |  |  | 8 | 20 | 0.3 |  |  | 72.5424
[19 empty] | SINGLE PHASE LOOKUPS |  | Single PH Motor REF |  | 8 | HP | #N/A |  |  | 9 | 25 | 0.3 |  |  | 72.5424
[28 empty] | 10 | 30 | 0.3 |  |  | 72.5424
[28 empty] | 11 | 40 | 0.3 |  |  | 72.5424
[28 empty] | 12 | 50 | 0.3 |  |  | 72.5424
[28 empty] | 13 | 60 | 0.3 |  |  | 72.5424
[28 empty] | 14 | 75 | 0.3 |  |  | 72.5424
[28 empty] | 15 | 100 | 0.3 |  |  | 72.5424
[28 empty] | 16 | 150 | 0.3 |  |  | 72.5424
[28 empty] | 17 | 200 | 0.3 |  |  | 72.5424
[28 empty] | 18 | 250 | 0.3 |  |  | 72.5424
[28 empty] | 19 | 300 | 0.3 |  |  | 72.5424
[28 empty] | 20 | 400 | 0.3 |  |  | 72.5424
[28 empty] | 21 | 500 | 0.3 |  |  | 72.5424
[28 empty] | 22 | 600 | 0.3 |  |  | 72.5424
[28 empty] | 23 | 700 | 0.3 |  |  | 72.5424
[28 empty] | 24 | 800 | 0.3 |  |  | 72.5424
[28 empty] | 25 | 900 | 0.3 |  |  | 72.5424
[28 empty] | 26 | 1000 | 0.3 |  |  | 72.5424
[28 empty] | 27 | 1200 | 0.3 |  |  | 72.5424
[28 empty] | 28 | 1500 | 0.3 |  |  | 72.5424

## UGSECVDROP3 (hidden)
[17 empty] | Ampicity | Check
Transformer | Trans Kw | [10 empty] | CONDUCTOR DATA DESIGN MANUAL |  |  |  |  | 1 PH | OK
15 | #REF! | [7 empty] | Wire Ref | 2 | ALUMINUM CABLES OHMS / 1000 FT |  |  |  | Volt Drop | Amp Check | 3 PH | #N/A
15 | 0 | [7 empty] | Volt Drop | 0 | SIZE | R | X | Z |  | 1 through 7 | 7 through 12
75 | 0 | [8 empty] | 1 | 2 | 0.267 | 0.0238 | 0.25067 | 0 | OK | NO
[10 empty] | 2 | 1/0 | 0.168 | 0.0241 | 0.1617 | 0 | OK | NO
[9 empty] | 1 | 3 | 3/0 | 0.105 | 0.0226 | 0.10435 | 0 | OK | NO
[9 empty] | 2 | 4 | 350 | 0.0505 | 0.0215 | 0.054822 | 0 | OK | NO
PF | ANGLE |  | 1-PH = 1 | SYSTEM |  | Cable Demand | KW |  | 3 | 5 | 500 | 0.0354 | 0.0207 | 0.040883 | 0 | OK | NO
0.9 | 25.8419 |  | 3-PH = 3 | 1 |  |  | 0 |  | 4 | 6 | 1000 | 0.0177 | 0.0199 | 0.024604 | 0 | OK | NO
VOLTAGE |  |  | RUN |  | FEET |  | L-AMPS |  |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C
120 | 240 |  | 1 |  | 0 |  | 0 |  |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | 600 Volt Secondary Aluminum Cable, DB Conduit (Direct Buried)
|  |  | IF 3 PH | [7 empty] | SIZE | R@65C | R@90C | X | Z | R@90C | Z |  | (With 7-1/2 Inches Centerline to Centerline Spacing Between Conduits)
|  |  | 1 | [7 empty] | 2 | 0.31061 | 0.33653 | 0.045 | 0.32249 | 0.2052 | 0.2043 |  | Cable Size | Conduit | Number of | Number of Runs
[11 empty] | 1 | 0.24432 | 0.26471 | 0.046 | 0.25829 | 0.1623 | 0.16612 |  | Size | Size | Conductors | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Single-Phase Transformers |  |  |  | Three-Phase Transformers | [6 empty] | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.2094 | 0.1334 | 0.13924 |  | 1000 | 5"DB | 3-1/C | 605 | 1104 | 1527 | 1892 | 2335 | 2526 | 2821 | 3080 | 3339 | 3550 | 3707 | 3828
[11 empty] | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.16944 | 0.1028 | 0.11126 |  | 500 | 4"DB | 3-1/C | 397 | 736 | 1029 | 1288 | 1595 | 1746 | 1953 | 2144 | 2313 | 2470 | 2607 | 2712
kVA |  | 15 |  | kVA |  | 75 |  |  |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.13724 | 0.0825 | 0.092557 |  | 350 | 3"DB | 2-1/C | 318 | 600 | 852 | 1076 | 1285 | 1482 | 1673 | 1840 | 2016 | 2160 | 2266 | 2376
Percentage Load |  | 111.1% |  | Percentage Load |  | N/A |  |  |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.11354 | 0.0653 | 0.076641 |  | 350 | 3"DB | 3-1/C | 313 | 586 | 822 | 1036 | 1230 | 1416 | 1589 | 1760 | 1908 | 2040 | 2145 | 2232
%Transformer Volt Drop |  | 2.3 |  | %Transformer Volt Drop |  | 0 |  |  |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.098578 | 0.0552 | 0.067551 |  | 3/0 | 2"DB | 2-1/C | 202 | 386 | 552 | 704 | 875 | 984 | 1113 | 1232 | 1250 | 1440 | 1518 | 1608
Load on Transformer |  | 15 | KW |  |  | 0 | KW |  |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075795 | 0.0404 | 0.053796 |  | 3/0 | 3"DB | 3-1/C | 199 | 376 | 534 | 676 | 810 | 936 | 1057 | 1160 | 1269 | 1350 | 1419 | 1500
[11 empty] | 500 | 0.042235 | 0.04576 | 0.039 | 0.058184 | 0.0289 | 0.04301 |  | 1/0 | 2"DB | 2-1/C | 152 | 292 | 420 | 536 | 645 | 750 | 854 | 944 | 1044 | 1130 | 1188 | 1248
[11 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.043965 | 0.0199 | 0.034474 |  | #2 | 2"DB | 2-1/C | 113 | 218 | 315 | 404 | 490 | 570 | 651 | 720 | 792 | 860 | 913 | 960
[11 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.037873 | 0.0157 | 0.030258 |  | #8 | 1"DB | 1/C | 47 | 92 | 135 | 176 | 215 | 252 | 287 | 320 | 306 | 380 | 407 | 432
Ampacity OK |  | ALUMINUM CABLES |  |  |  | COPPER CABLES
Yes or No | Yes or No |  |  |  | TRANS. + CABLE |  |  | TRANS. + CABLE |  |  |  | 0.023 | 0.024115 |  | 0.077 | 0.080732
1-7 Runs | 8-12 Runs | SIZE | V - DROP | % DROP | %V-DROP | V - DROP | % DROP | V-DROP
OK | NO | 2 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Single Phase Padmount Transformer Size
|  | 1 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [11 empty] | kVA
OK | NO | 1/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Percentage | 15 | 25 | Number of Runs 1: 50; Number of Runs 2: 75; Number of Runs 3: 100; Number of Runs 4: 167; Number of Runs 5: Under 50% Loading
|  | 2/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 50% | 1 | 1 | Number of Runs 1: 1; Number of Runs 2: 0.9; Number of Runs 3: 0.9; Number of Runs 4: 1; Number of Runs 6: #N/A
OK | NO | 3/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 60% | 1.2 | 1.2 | Number of Runs 1: 1.2; Number of Runs 2: 1.1; Number of Runs 3: 1; Number of Runs 4: 1.2; Number of Runs 5: Over 50% Loading
|  | 4/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 70% | 1.5 | 1.4 | Number of Runs 1: 1.4; Number of Runs 2: 1.3; Number of Runs 3: 1.2; Number of Runs 4: 1.4; Number of Runs 6: 2.3
|  | 250 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 50 |  | 80% | 1.7 | 1.6 | Number of Runs 1: 1.6; Number of Runs 2: 1.5; Number of Runs 3: 1.4; Number of Runs 4: 1.6
OK | NO | 350 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 90% | 1.9 | 1.8 | Number of Runs 1: 1.8; Number of Runs 2: 1.6; Number of Runs 3: 1.6; Number of Runs 4: 1.8
OK | NO | 500 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | #VALUE! |  | 100% | 2.1 | 2 | Number of Runs 1: 1.8; Number of Runs 2: 1.8; Number of Runs 3: 1.7; Number of Runs 4: 2
|  | 750 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 60% |  | 110% | 2.3 | 2.2 | Number of Runs 1: 2; Number of Runs 2: 2; Number of Runs 3: 1.9; Number of Runs 4: 2.2
OK | NO | 1000 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 0 |  | 120% | 2.5 | 2.4 | Number of Runs 1: 2.2; Number of Runs 2: 2.2; Number of Runs 3: 2.1; Number of Runs 4: 2.4
[17 empty] | 0 |  | 130% | 2.7 | 2.6 | Number of Runs 1: 2.4; Number of Runs 2: 2.4; Number of Runs 3: 2.3; Number of Runs 4: 2.6
[19 empty] | 140% | 2.9 | 2.8 | Number of Runs 1: 2.6; Number of Runs 2: 2.5; Number of Runs 3: 2.4; Number of Runs 4: 2.9
[17 empty] | 1.35 |  | 150% | 3.1 | 3 | Number of Runs 1: 2.8; Number of Runs 2: 2.7; Number of Runs 3: 2.6; Number of Runs 4: 3.1
[17 empty] | 1 |  | 160% | 3.3 | 3.2 | Number of Runs 1: 2.9; Number of Runs 2: 2.9; Number of Runs 3: 2.8; Number of Runs 4: 3.3
Number of Runs | [16 empty] | 50kVA |  | 170% | 3.5 | 3.4 | Number of Runs 1: 3; Number of Runs 2: 3.1; Number of Runs 3: 3.3; Number of Runs 4: 3.6
1 | [16 empty] | 70%
2 | [16 empty] | #N/A |  | 120/208V Three-Phase Padmount Transformer Size
3 | [18 empty] | Transformer | Kva
4 | [18 empty] | Loading | 45 | 75 | Number of Runs 1: 150; Number of Runs 2: 225; Number of Runs 3: 300; Number of Runs 4: 500; Number of Runs 5: 750; Number of Runs 6: 1000
5 | [18 empty] | 50% | 1.3 | 1.13 | Number of Runs 1: 0.89; Number of Runs 2: 0.91; Number of Runs 3: 0.98; Number of Runs 4: 1.54; Number of Runs 5: 2.03; Number of Runs 6: 1.9
6 | [18 empty] | 60% | 1.6 | 1.35 | Number of Runs 1: 1.07; Number of Runs 2: 1.1; Number of Runs 3: 1.17; Number of Runs 4: 1.8; Number of Runs 5: 2.43; Number of Runs 6: 2.33
7 | [18 empty] | 70% | 1.8 | 1.58 | Number of Runs 1: 1.2; Number of Runs 2: 1.3; Number of Runs 3: 1.37; Number of Runs 4: 2.1; Number of Runs 5: 2.84; Number of Runs 6: 2.72
8 | [18 empty] | 80% | 2.1 | 1.81 | Number of Runs 1: 1.43; Number of Runs 2: 1.46; Number of Runs 3: 1.56; Number of Runs 4: 2.4; Number of Runs 5: 3.2; Number of Runs 6: 3
9 | [18 empty] | 90% | 2.4 | 2.03 | Number of Runs 1: 1.6; Number of Runs 2: 1.64; Number of Runs 3: 1.76; Number of Runs 4: 2.7; Number of Runs 5: 3.6; Number of Runs 6: 3.4
10 | [18 empty] | 100% | 2.6 | 2.26 | Number of Runs 1: 1.78; Number of Runs 2: 1.83; Number of Runs 3: 1.9; Number of Runs 4: 3; Number of Runs 5: 4; Number of Runs 6: 3.8
11 | [18 empty] | 110% | 2.9 | 2.48 | Number of Runs 1: 1.96; Number of Runs 2: 2.01; Number of Runs 3: 2.1; Number of Runs 4: 3.3; Number of Runs 5: 4.3; Number of Runs 6: 4.2
12 | [18 empty] | 120% | 3.2 | 2.71 | Number of Runs 1: 2.14; Number of Runs 2: 2.2; Number of Runs 3: 2.3; Number of Runs 4: 3.6; Number of Runs 5: 4.7; Number of Runs 6: 4.6
[19 empty] | 130% | 3.4 | 2.94 | Number of Runs 1: 2.39; Number of Runs 2: 2.49; Number of Runs 3: 2.72; Number of Runs 4: 4; Number of Runs 5: 5.4; Number of Runs 6: 5.2
[19 empty] | 140% | 3.7 | 3.16 | Number of Runs 1: 2.57; Number of Runs 2: 2.68; Number of Runs 3: 2.93; Number of Runs 4: 4.44; Number of Runs 5: 5.9; Number of Runs 6: 5.6
[19 empty] | 150% | 4 | 3.69 | Number of Runs 1: 2.91; Number of Runs 2: 3.07; Number of Runs 3: 3.37; Number of Runs 4: 5; Number of Runs 5: 6.8; Number of Runs 6: 6.5; Number of Runs 7: Under 50% Loading
#N/A
Over 50% Loading
[19 empty] | 277/480V Three-Phase Padmount Transformer Size |  |  | Number of Runs 8: 0
[19 empty] | Transformer | Kva
[19 empty] | Loading | 75 | 150 | 225 | 300 | 500 | 750 | 1000 | 1500 | 2000 | 2500 | 3000
[19 empty] | 50% | 1.07 | 0.92 | 0.72 | 0.96 | 0.93 | 1.93 | 1.9 | 1.9 | 1.8 | 1.8 | 1.9
[19 empty] | 60% | 1.29 | 1.1 | 0.87 | 1.15 | 1.12 | 2.32 | 2.34 | 2.34 | 2.2 | 2.2 | 2.2
[19 empty] | 70% | 1.5 | 1.3 | 1.01 | 1.3 | 1.3 | 2.6 | 2.73 | 2.6 | 2.63 | 2.6 | 2.6
[19 empty] | 80% | 1.72 | 1.47 | 1.16 | 1.54 | 1.49 | 3 | 3 | 3 | 2.9 | 3.04 | 3
[19 empty] | 90% | 1.93 | 1.65 | 1.3 | 1.73 | 1.68 | 3.4 | 3.4 | 3.4 | 3.3 | 3.3 | 3.3
[19 empty] | 100% | 2.1 | 1.84 | 1.4 | 1.92 | 1.86 | 3.8 | 3.8 | 3.8 | 3.7 | 3.7 | 3.7
[19 empty] | 110% | 2.36 | 2.02 | 1.59 | 2.11 | 2 | 4.1 | 4.2 | 4.2 | 4 | 4.1 | 4.1
[19 empty] | 120% | 2.58 | 2.21 | 1.73 | 2.31 | 2.24 | 4.5 | 4.6 | 4.5 | 4.4 | 4.4 | 4.4
[19 empty] | 130% | 2.79 | 2.5 | 1.88 | 2.6 | 2.5 | 5.2 | 5.2 | 5.3 | 5.1 | 5.2 | 5.2
[19 empty] | 140% | 3.01 | 2.6 | 2.1 | 2.8 | 2.7 | 5.6 | 5.6 | 5.7 | 5.5 | 5.6 | 5.7
[19 empty] | 150% | 3.5 | 3 | 2.4 | 3.3 | 3.1 | 6.4 | 65 | 6.5 | 6.3 | 6.4 | 6.5
2

## UGSECFLCKER3 (hidden)
[34 empty] | 15 | 2.1 | 1.7 | 1.2 | updated 17th Feb. 2000 with table 5 of 5413.7
[34 empty] | 25 | 2 | 1.6 | 1.2
[34 empty] | 50 | 2.1 | 1.3 | 1.7
[34 empty] | 75 | 2 | 1.1 | 1.8 | 1.051 | 1.751
[34 empty] | 100 | 2.2 | 1.1 | 1.9
[17 empty] | LRC VALUES (updated 5 FEB 1998) | [15 empty] | Single Phase kVA | 167 | 2.3 | 1.1 | 2
[18 empty] | SINGLE-PHASE MOTOR SIZES IN HP | [15 empty] | 45 | 2.7153 | 1.91 | 1.93
[17 empty] | VOLTAGE | 1 | 1.5 | 2 | [13 empty] | 75 | 2.2888 | 1.72 | 1.51 | 1.62 | 1.46
[17 empty] | 120 | 46 | 69 | 92 | [13 empty] | 150 | 1.916 | 1.14 | 1.54
[34 empty] | 225 | 1.9462 | 1.19 | 1.54
[11 empty] | CONDUCTOR DATA DESIGN MANUAL | [22 empty] | 300 | 2.2897 | 1.02 | 2.05
PF | ANGLE | 1-PH = 1 | # OF PHASES | HP |  | 1Ph-LRC | 1Ph-XKMR% |  |  | ALUMINUM CABLES OHMS / 1000 FT | [23 empty] | 500 | 4.5034 | 0.81 | 4.43
0.75 | 41.4096 | 3-PH = 3 | 1 | 4.5 |  | 103 | 3.4093 | 1.7 | 1-Ph | SIZE | R | X | Z | L-AMPS |  |  | LRC VALUES (updated 5 FEB 1998) | [16 empty] | 750 | 6.0451 | 0.95 | 5.97
[6 empty] | 3Ph-LRC |  | #N/A | 3-Ph | 2 | 0.267 | 0.0238 | 0.21599 | 103 |  |  |  | SINGLE-PHASE MOTOR SIZES IN HORSE POWER | [15 empty] | 1000 | 5.82 | 0.9 | 5.75
[6 empty] | n/a |  | X |  | 1/0 | 0.168 | 0.0241 | 0.14194 |  |  |  | VOLTAGE | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 10 | [7 empty] | 1500 | 0 | 0 | 0
VOLTAGE |  | RUN | FEET | KW |  | XFMR KVA | 3Ph-XFMR % | 1.2 | 1-Ph | 3/0 | 0.105 | 0.0226 | 0.093698 |  |  |  | 240 | 27 | 34 | 46 | 69 | 103 | 115 | 140 | 175 | 218 | [7 empty] | 2000 | 0 | 0 | 0
120 | 240 | 1 | 0 | 18.54 |  | 15 | 0 | #N/A |  | 350 | 0.0505 | 0.0215 | 0.052096 | [20 empty] | 2500 | 0 | 0 | 0
[10 empty] | 500 | 0.0354 | 0.0207 | 0.040242 | [20 empty] | 3000 | 0 | 0 | 0
ALUMINUM CABLES |  |  |  | COPPER CABLES | [28 empty] | Three Phase kVA | Three Phase kVA | Z% | R% | X%
| CABLE | CABLE | *TOTAL% | CABLE |  | CABLE | *TOTAL% |  |  | 1000 | 0.0177 | 0.0199 | 0.026438 | [20 empty] | updated 17th Feb. 2000 with table 9 of 5413.7
SIZE | (VOLTS) | ( % ) | FLICKER | (VOLTS) |  | ( % ) | FLICKER |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C | [6 empty] | LRC VALUES (updated 31dec1997)
2 | 0 | 0 | 3.4093 | 0 |  | 0 | 0 |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | MOTOR SIZES IN HORSE POWER
1 | 0 | 0 | 3.4093 | 0 |  | 0 | 0 |  |  | SIZE | R@65C | R@90C | X | Z | R@90C | Z | VOLTAGE | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200
1/0 | 0 | 0 | 3.4093 | 0 |  | 0 | 0 |  |  | 2 | 0.31061 | 0.33653 | 0.045 | 0.28216 | 0.2052 | 0.18366 | 208 | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
2/0 | 0 | 0 | 3.4093 | 0 |  | 0 | 0 |  |  | 1 | 0.24432 | 0.26471 | 0.046 | 0.22896 | 0.1623 | 0.15215 | 240 | 64 | 85 | 92 | 106 | 127 | 162 | 232 | 290 | 365 | 435 | 580 | 725 | 1085 | 1450 | 2170
3/0 | 0 | 0 | 3.4093 | 0 |  | 0 | 0 |  |  | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.18762 | 0.1334 | 0.12915 | 480 | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
4/0 | 0 | 0 | 3.4093 | 0 |  | 0 | 0 |  |  | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.15403 | 0.1028 | 0.10554
250 | 0 | 0 | 3.4093 | 0 |  | 0 | 0 |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.12689 | 0.0825 | 0.089655
350 | 0 | 0 | 3.4093 | 0 |  | 0 | 0 |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.10684 | 0.0653 | 0.076094
500 | 0 | 0 | 3.4093 | 0 |  | 0 | 0 |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.094374 | 0.0552 | 0.068519
750 | 0 | 0 | 3.4093 | 0 |  | 0 | 0 |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075091 | 0.0404 | 0.056758 |  | 3 Phase | Three-Phase Motor (Sized in HP) | [15 empty] | Transformer Data |  | X/R
1000 | 0 | 0 | 3.4093 | 0 |  | 0 | 0 |  |  | 500 | 0.042235 | 0.04576 | 0.039 | 0.060116 | 0.0289 | 0.047471 |  | Trans | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200 | R | X | Ratio | Z%
[10 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.047969 | 0.0199 | 0.04006 |  | 45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.0191 | 0.0193 | 1.0105 | 2.715%
[10 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.042594 | 0.0157 | 0.036248 |  | 75 | 0.66522 | 0.88072 | 0.95567 | 1.0962 | 1.3117 | 1.6771 | 2.4079 | 3.0076 | 3.7852 | 4.5066 | 6.0057 | 7.5142 | 11.2432 | 15.019 | 22.4864 | 30.0474 | 0.0172 | 0.0151 | 0.87791 | 2.289%
WITH REDUCED LRC TO 770A OR 50HP |  |  |  | *TOTAL FLICKER = CABLE (%) + XMFR (%) | [13 empty] | 150 | 0.3078 | 0.40751 | 0.44219 | 0.54094 | 0.60693 | 0.776 | 1.1141 | 1.3916 | 1.7514 | 2.0852 | 2.7789 | 3.4768 | 5.2022 | 6.9493 | 10.4045 | 13.903 | 0.0114 | 0.0154 | 1.3509 | 1.916%
[11 empty] | 0.023 | 0.024115 |  | 0.077 | 0.080732 |  |  | 225 | 0.20691 | 0.27393 | 0.29724 | 0.34096 | 0.40798 | 0.52163 | 0.74894 | 0.93544 | 1.1773 | 1.4017 | 1.868 | 2.3372 | 3.497 | 4.6714 | 6.994 | 9.3457 | 0.0119 | 0.0154 | 1.2941 | 1.946%
[18 empty] | 300 | 0.19214 | 0.25438 | 0.27603 | 0.31663 | 0.37887 | 0.48441 | 0.69549 | 0.86869 | 1.0933 | 1.3017 | 1.7347 | 2.1704 | 3.2474 | 4.338 | 6.4949 | 8.6788 | 0.0102 | 0.0205 | 2.0098 | 2.29%
Lookup Value |  | 0 | [15 empty] | 500 | 0.22773 | 0.3015 | 0.32716 | 0.37527 | 0.44904 | 0.57413 | 0.82432 | 1.0296 | 1.2958 | 1.5428 | 2.056 | 2.5724 | 3.8489 | 5.1415 | 7.6979 | 10.2863 | 0.0081 | 0.0443 | 5.4691 | 4.503%
Lookup | Wire | Volatge Drop | % Volatge Drop | SER 5 | SER 10 | X% | [11 empty] | 750 | 0.20315 | 0.26896 | 0.29185 | 0.33476 | 0.40057 | 0.51216 | 0.73534 | 0.91846 | 1.1559 | 1.3763 | 1.8341 | 2.2947 | 3.4335 | 4.5866 | 6.867 | 9.176 | 0.0095 | 0.0597 | 6.2842 | 6.045%
1 | 2 | 0 | 0 | 0.28216 | 0.28216 | 0.045 | SER5 | 0 | [9 empty] | 1000 | 0.14663 | 0.19413 | 0.21065 | 0.24163 | 0.28913 | 0.36968 | 0.53076 | 0.66294 | 0.83435 | 0.99337 | 1.3238 | 1.6563 | 2.4783 | 3.3106 | 4.9565 | 6.6232 | 0.009 | 0.0575 | 6.3889 | 5.82%
2 | 1/0 | 0 | 0 | 0.18762 | 0.18762 | 0.044 | SER10 | 0 | [9 empty] | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
3 | 3/0 | 0 | 0 | 0.12689 | 0.12689 | 0.042 | [11 empty] | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
4 | 350 | 0 | 0 | 0.075091 | 0.075091 | 0.04 | [11 empty] | 2500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
5 | 500 | 0 | 0 | 0.060116 | 0.060116 | 0.039 | [11 empty] | 3000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
6 | 1000 | 0 | 0 | [14 empty] | Locked Rotor Current
[18 empty] | @208V | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
[18 empty] | @480V | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
1 Phase
Trans
(kVA)
25
50
75
100
[18 empty] | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE |  |  | Three Phase Motor Data |  | Three PH Motor REF | 9 | HP | #N/A
[18 empty] | 1 | 1 |  |  | 1HP | 0.75 | 41.4096 |  |  | LOOKUP | HP | P.F. | REF
[18 empty] | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096 |  |  | 1 | 3 | 0.3 | 11 | SER 1 | 72.5424
[18 empty] | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096 |  |  | 2 | 4.5 | 0.3 | 14 | SER 2 | 72.5424
[18 empty] | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096 |  |  | 3 | 5 | 0.3 | 9 | SER 3 | 72.5424
[18 empty] | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096 |  |  | 4 | 6 | 0.3 |  | SEC 1 | 72.5424
[18 empty] | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096 |  |  | 5 | 7.5 | 0.3 |  |  | 72.5424
[18 empty] | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096 |  |  | 6 | 10 | 0.3 |  |  | 72.5424
[18 empty] | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096 |  |  | 7 | 15 | 0.3 |  |  | 72.5424
[18 empty] | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096 |  |  | 8 | 20 | 0.3 |  |  | 72.5424
[18 empty] | SINGLE PHASE LOOKUPS |  | Single PH Motor REF |  | 5 | HP | #N/A |  |  | 9 | 25 | 0.3 |  |  | 72.5424
[27 empty] | 10 | 30 | 0.3 |  |  | 72.5424
[27 empty] | 11 | 40 | 0.3 |  |  | 72.5424
[27 empty] | 12 | 50 | 0.3 |  |  | 72.5424
[27 empty] | 13 | 60 | 0.3 |  |  | 72.5424
[27 empty] | 14 | 75 | 0.3 |  |  | 72.5424
[27 empty] | 15 | 100 | 0.3 |  |  | 72.5424
[27 empty] | 16 | 150 | 0.3 |  |  | 72.5424
[27 empty] | 17 | 200 | 0.3 |  |  | 72.5424
[27 empty] | 18 | 250 | 0.3 |  |  | 72.5424
[27 empty] | 19 | 300 | 0.3 |  |  | 72.5424
[27 empty] | 20 | 400 | 0.3 |  |  | 72.5424
[27 empty] | 21 | 500 | 0.3 |  |  | 72.5424
[27 empty] | 22 | 600 | 0.3 |  |  | 72.5424
[27 empty] | 23 | 700 | 0.3 |  |  | 72.5424
[27 empty] | 24 | 800 | 0.3 |  |  | 72.5424
[27 empty] | 25 | 900 | 0.3 |  |  | 72.5424
[27 empty] | 26 | 1000 | 0.3 |  |  | 72.5424
[27 empty] | 27 | 1200 | 0.3 |  |  | 72.5424
[27 empty] | 28 | 1500 | 0.3 |  |  | 72.5424

## UGSECVDROP4 (hidden)
[17 empty] | Ampicity | Check
Transformer | Trans Kw | [10 empty] | CONDUCTOR DATA DESIGN MANUAL |  |  |  |  | 1 PH | OK
15 | #REF! | [7 empty] | Wire Ref | 2 | ALUMINUM CABLES OHMS / 1000 FT |  |  |  | Volt Drop | Amp Check | 3 PH | #N/A
15 | 0 | [7 empty] | Volt Drop | 0 | SIZE | R | X | Z |  | 1 through 7 | 7 through 12
75 | 0 | [8 empty] | 1 | 2 | 0.267 | 0.0238 | 0.25067 | 0 | OK | NO
[10 empty] | 2 | 1/0 | 0.168 | 0.0241 | 0.1617 | 0 | OK | NO
[9 empty] | 1 | 3 | 3/0 | 0.105 | 0.0226 | 0.10435 | 0 | OK | NO
[9 empty] | 2 | 4 | 350 | 0.0505 | 0.0215 | 0.054822 | 0 | OK | NO
PF | ANGLE |  | 1-PH = 1 | SYSTEM |  | Cable Demand | KW |  | 3 | 5 | 500 | 0.0354 | 0.0207 | 0.040883 | 0 | OK | NO
0.9 | 25.8419 |  | 3-PH = 3 | 1 |  |  | 0 |  | 4 | 6 | 1000 | 0.0177 | 0.0199 | 0.024604 | 0 | OK | NO
VOLTAGE |  |  | RUN |  | FEET |  | L-AMPS |  |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C
120 | 240 |  | 1 |  | 0 |  | 0 |  |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | 600 Volt Secondary Aluminum Cable, DB Conduit (Direct Buried)
|  |  | IF 3 PH | [7 empty] | SIZE | R@65C | R@90C | X | Z | R@90C | Z |  | (With 7-1/2 Inches Centerline to Centerline Spacing Between Conduits)
|  |  | 1 | [7 empty] | 2 | 0.31061 | 0.33653 | 0.045 | 0.32249 | 0.2052 | 0.2043 |  | Cable Size | Conduit | Number of | Number of Runs
[11 empty] | 1 | 0.24432 | 0.26471 | 0.046 | 0.25829 | 0.1623 | 0.16612 |  | Size | Size | Conductors | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Single-Phase Transformers |  |  |  | Three-Phase Transformers | [6 empty] | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.2094 | 0.1334 | 0.13924 |  | 1000 | 5"DB | 3-1/C | 605 | 1104 | 1527 | 1892 | 2335 | 2526 | 2821 | 3080 | 3339 | 3550 | 3707 | 3828
[11 empty] | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.16944 | 0.1028 | 0.11126 |  | 500 | 4"DB | 3-1/C | 397 | 736 | 1029 | 1288 | 1595 | 1746 | 1953 | 2144 | 2313 | 2470 | 2607 | 2712
kVA |  | 15 |  | kVA |  | 75 |  |  |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.13724 | 0.0825 | 0.092557 |  | 350 | 3"DB | 2-1/C | 318 | 600 | 852 | 1076 | 1285 | 1482 | 1673 | 1840 | 2016 | 2160 | 2266 | 2376
Percentage Load |  | 111.1% |  | Percentage Load |  | N/A |  |  |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.11354 | 0.0653 | 0.076641 |  | 350 | 3"DB | 3-1/C | 313 | 586 | 822 | 1036 | 1230 | 1416 | 1589 | 1760 | 1908 | 2040 | 2145 | 2232
%Transformer Volt Drop |  | 2.3 |  | %Transformer Volt Drop |  | 0 |  |  |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.098578 | 0.0552 | 0.067551 |  | 3/0 | 2"DB | 2-1/C | 202 | 386 | 552 | 704 | 875 | 984 | 1113 | 1232 | 1250 | 1440 | 1518 | 1608
Load on Transformer |  | 15 | KW |  |  | 0 | KW |  |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075795 | 0.0404 | 0.053796 |  | 3/0 | 3"DB | 3-1/C | 199 | 376 | 534 | 676 | 810 | 936 | 1057 | 1160 | 1269 | 1350 | 1419 | 1500
[11 empty] | 500 | 0.042235 | 0.04576 | 0.039 | 0.058184 | 0.0289 | 0.04301 |  | 1/0 | 2"DB | 2-1/C | 152 | 292 | 420 | 536 | 645 | 750 | 854 | 944 | 1044 | 1130 | 1188 | 1248
[11 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.043965 | 0.0199 | 0.034474 |  | #2 | 2"DB | 2-1/C | 113 | 218 | 315 | 404 | 490 | 570 | 651 | 720 | 792 | 860 | 913 | 960
[11 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.037873 | 0.0157 | 0.030258 |  | #8 | 1"DB | 1/C | 47 | 92 | 135 | 176 | 215 | 252 | 287 | 320 | 306 | 380 | 407 | 432
Ampacity OK |  | ALUMINUM CABLES |  |  |  | COPPER CABLES
Yes or No | Yes or No |  |  |  | TRANS. + CABLE |  |  | TRANS. + CABLE |  |  |  | 0.023 | 0.024115 |  | 0.077 | 0.080732
1-7 Runs | 8-12 Runs | SIZE | V - DROP | % DROP | %V-DROP | V - DROP | % DROP | V-DROP
OK | NO | 2 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Single Phase Padmount Transformer Size
|  | 1 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [11 empty] | kVA
OK | NO | 1/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | Percentage | 15 | 25 | Number of Runs 1: 50; Number of Runs 2: 75; Number of Runs 3: 100; Number of Runs 4: 167; Number of Runs 5: Under 50% Loading
|  | 2/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 50% | 1 | 1 | Number of Runs 1: 1; Number of Runs 2: 0.9; Number of Runs 3: 0.9; Number of Runs 4: 1; Number of Runs 6: #N/A
OK | NO | 3/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 60% | 1.2 | 1.2 | Number of Runs 1: 1.2; Number of Runs 2: 1.1; Number of Runs 3: 1; Number of Runs 4: 1.2; Number of Runs 5: Over 50% Loading
|  | 4/0 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 70% | 1.5 | 1.4 | Number of Runs 1: 1.4; Number of Runs 2: 1.3; Number of Runs 3: 1.2; Number of Runs 4: 1.4; Number of Runs 6: 2.3
|  | 250 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 50 |  | 80% | 1.7 | 1.6 | Number of Runs 1: 1.6; Number of Runs 2: 1.5; Number of Runs 3: 1.4; Number of Runs 4: 1.6
OK | NO | 350 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [10 empty] | 90% | 1.9 | 1.8 | Number of Runs 1: 1.8; Number of Runs 2: 1.6; Number of Runs 3: 1.6; Number of Runs 4: 1.8
OK | NO | 500 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | #VALUE! |  | 100% | 2.1 | 2 | Number of Runs 1: 1.8; Number of Runs 2: 1.8; Number of Runs 3: 1.7; Number of Runs 4: 2
|  | 750 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 60% |  | 110% | 2.3 | 2.2 | Number of Runs 1: 2; Number of Runs 2: 2; Number of Runs 3: 1.9; Number of Runs 4: 2.2
OK | NO | 1000 | 0 | 0 | 2.3 | 0 | 0 | 2.3 | [8 empty] | 0 |  | 120% | 2.5 | 2.4 | Number of Runs 1: 2.2; Number of Runs 2: 2.2; Number of Runs 3: 2.1; Number of Runs 4: 2.4
[17 empty] | 0 |  | 130% | 2.7 | 2.6 | Number of Runs 1: 2.4; Number of Runs 2: 2.4; Number of Runs 3: 2.3; Number of Runs 4: 2.6
[19 empty] | 140% | 2.9 | 2.8 | Number of Runs 1: 2.6; Number of Runs 2: 2.5; Number of Runs 3: 2.4; Number of Runs 4: 2.9
[17 empty] | 1.35 |  | 150% | 3.1 | 3 | Number of Runs 1: 2.8; Number of Runs 2: 2.7; Number of Runs 3: 2.6; Number of Runs 4: 3.1
[17 empty] | 1 |  | 160% | 3.3 | 3.2 | Number of Runs 1: 2.9; Number of Runs 2: 2.9; Number of Runs 3: 2.8; Number of Runs 4: 3.3
Number of Runs | [16 empty] | 50kVA |  | 170% | 3.5 | 3.4 | Number of Runs 1: 3; Number of Runs 2: 3.1; Number of Runs 3: 3.3; Number of Runs 4: 3.6
1 | [16 empty] | 70%
2 | [16 empty] | #N/A |  | 120/208V Three-Phase Padmount Transformer Size
3 | [18 empty] | Transformer | Kva
4 | [18 empty] | Loading | 45 | 75 | Number of Runs 1: 150; Number of Runs 2: 225; Number of Runs 3: 300; Number of Runs 4: 500; Number of Runs 5: 750; Number of Runs 6: 1000
5 | [18 empty] | 50% | 1.3 | 1.13 | Number of Runs 1: 0.89; Number of Runs 2: 0.91; Number of Runs 3: 0.98; Number of Runs 4: 1.54; Number of Runs 5: 2.03; Number of Runs 6: 1.9
6 | [18 empty] | 60% | 1.6 | 1.35 | Number of Runs 1: 1.07; Number of Runs 2: 1.1; Number of Runs 3: 1.17; Number of Runs 4: 1.8; Number of Runs 5: 2.43; Number of Runs 6: 2.33
7 | [18 empty] | 70% | 1.8 | 1.58 | Number of Runs 1: 1.2; Number of Runs 2: 1.3; Number of Runs 3: 1.37; Number of Runs 4: 2.1; Number of Runs 5: 2.84; Number of Runs 6: 2.72
8 | [18 empty] | 80% | 2.1 | 1.81 | Number of Runs 1: 1.43; Number of Runs 2: 1.46; Number of Runs 3: 1.56; Number of Runs 4: 2.4; Number of Runs 5: 3.2; Number of Runs 6: 3
9 | [18 empty] | 90% | 2.4 | 2.03 | Number of Runs 1: 1.6; Number of Runs 2: 1.64; Number of Runs 3: 1.76; Number of Runs 4: 2.7; Number of Runs 5: 3.6; Number of Runs 6: 3.4
10 | [18 empty] | 100% | 2.6 | 2.26 | Number of Runs 1: 1.78; Number of Runs 2: 1.83; Number of Runs 3: 1.9; Number of Runs 4: 3; Number of Runs 5: 4; Number of Runs 6: 3.8
11 | [18 empty] | 110% | 2.9 | 2.48 | Number of Runs 1: 1.96; Number of Runs 2: 2.01; Number of Runs 3: 2.1; Number of Runs 4: 3.3; Number of Runs 5: 4.3; Number of Runs 6: 4.2
12 | [18 empty] | 120% | 3.2 | 2.71 | Number of Runs 1: 2.14; Number of Runs 2: 2.2; Number of Runs 3: 2.3; Number of Runs 4: 3.6; Number of Runs 5: 4.7; Number of Runs 6: 4.6
[19 empty] | 130% | 3.4 | 2.94 | Number of Runs 1: 2.39; Number of Runs 2: 2.49; Number of Runs 3: 2.72; Number of Runs 4: 4; Number of Runs 5: 5.4; Number of Runs 6: 5.2
[19 empty] | 140% | 3.7 | 3.16 | Number of Runs 1: 2.57; Number of Runs 2: 2.68; Number of Runs 3: 2.93; Number of Runs 4: 4.44; Number of Runs 5: 5.9; Number of Runs 6: 5.6
[19 empty] | 150% | 4 | 3.69 | Number of Runs 1: 2.91; Number of Runs 2: 3.07; Number of Runs 3: 3.37; Number of Runs 4: 5; Number of Runs 5: 6.8; Number of Runs 6: 6.5; Number of Runs 7: Under 50% Loading
#N/A
Over 50% Loading
[19 empty] | 277/480V Three-Phase Padmount Transformer Size |  |  | Number of Runs 8: 0
[19 empty] | Transformer | Kva
[19 empty] | Loading | 75 | 150 | 225 | 300 | 500 | 750 | 1000 | 1500 | 2000 | 2500 | 3000
[19 empty] | 50% | 1.07 | 0.92 | 0.72 | 0.96 | 0.93 | 1.93 | 1.9 | 1.9 | 1.8 | 1.8 | 1.9
[19 empty] | 60% | 1.29 | 1.1 | 0.87 | 1.15 | 1.12 | 2.32 | 2.34 | 2.34 | 2.2 | 2.2 | 2.2
[19 empty] | 70% | 1.5 | 1.3 | 1.01 | 1.3 | 1.3 | 2.6 | 2.73 | 2.6 | 2.63 | 2.6 | 2.6
[19 empty] | 80% | 1.72 | 1.47 | 1.16 | 1.54 | 1.49 | 3 | 3 | 3 | 2.9 | 3.04 | 3
[19 empty] | 90% | 1.93 | 1.65 | 1.3 | 1.73 | 1.68 | 3.4 | 3.4 | 3.4 | 3.3 | 3.3 | 3.3
[19 empty] | 100% | 2.1 | 1.84 | 1.4 | 1.92 | 1.86 | 3.8 | 3.8 | 3.8 | 3.7 | 3.7 | 3.7
[19 empty] | 110% | 2.36 | 2.02 | 1.59 | 2.11 | 2 | 4.1 | 4.2 | 4.2 | 4 | 4.1 | 4.1
[19 empty] | 120% | 2.58 | 2.21 | 1.73 | 2.31 | 2.24 | 4.5 | 4.6 | 4.5 | 4.4 | 4.4 | 4.4
[19 empty] | 130% | 2.79 | 2.5 | 1.88 | 2.6 | 2.5 | 5.2 | 5.2 | 5.3 | 5.1 | 5.2 | 5.2
[19 empty] | 140% | 3.01 | 2.6 | 2.1 | 2.8 | 2.7 | 5.6 | 5.6 | 5.7 | 5.5 | 5.6 | 5.7
[19 empty] | 150% | 3.5 | 3 | 2.4 | 3.3 | 3.1 | 6.4 | 65 | 6.5 | 6.3 | 6.4 | 6.5
2

## UGSECFLCKER4 (hidden)
[34 empty] | 15 | 2.1 | 1.7 | 1.2 | updated 17th Feb. 2000 with table 5 of 5413.7
[34 empty] | 25 | 2 | 1.6 | 1.2
[34 empty] | 50 | 2.1 | 1.3 | 1.7
[34 empty] | 75 | 2 | 1.1 | 1.8 | 1.051 | 1.751
[34 empty] | 100 | 2.2 | 1.1 | 1.9
[17 empty] | LRC VALUES (updated 5 FEB 1998) | [15 empty] | Single Phase kVA | 167 | 2.3 | 1.1 | 2
[18 empty] | SINGLE-PHASE MOTOR SIZES IN HP | [15 empty] | 45 | 2.7153 | 1.91 | 1.93
[17 empty] | VOLTAGE | 1 | 1.5 | 2 | [13 empty] | 75 | 2.2888 | 1.72 | 1.51 | 1.62 | 1.46
[17 empty] | 120 | 46 | 69 | 92 | [13 empty] | 150 | 1.916 | 1.14 | 1.54
[34 empty] | 225 | 1.9462 | 1.19 | 1.54
[11 empty] | CONDUCTOR DATA DESIGN MANUAL | [22 empty] | 300 | 2.2897 | 1.02 | 2.05
PF | ANGLE | 1-PH = 1 | # OF PHASES | HP |  | 1Ph-LRC | 1Ph-XKMR% | R |  | ALUMINUM CABLES OHMS / 1000 FT | [23 empty] | 500 | 4.5034 | 0.81 | 4.43
0.75 | 41.4096 | 3-PH = 3 | 1 | 6 |  | 140 | 4.6339 | 1.7 | 1-Ph | SIZE | R | X | Z | L-AMPS |  |  | LRC VALUES (updated 5 FEB 1998) | [16 empty] | 750 | 6.0451 | 0.95 | 5.97
[6 empty] | 3Ph-LRC |  | #N/A | 3-Ph | 2 | 0.267 | 0.0238 | 0.21599 | 140 |  |  |  | SINGLE-PHASE MOTOR SIZES IN HORSE POWER | [15 empty] | 1000 | 5.82 | 0.9 | 5.75
[6 empty] | n/a |  | X |  | 1/0 | 0.168 | 0.0241 | 0.14194 |  |  |  | VOLTAGE | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 10 | [7 empty] | 1500 | 0 | 0 | 0
VOLTAGE |  | RUN | FEET | KW |  | XFMR KVA | 3Ph-XFMR % | 1.2 | 1-Ph | 3/0 | 0.105 | 0.0226 | 0.093698 |  |  |  | 240 | 27 | 34 | 46 | 69 | 103 | 115 | 140 | 175 | 218 | [7 empty] | 2000 | 0 | 0 | 0
120 | 240 | 1 | 0 | 25.2 |  | 15 | 0 | #N/A |  | 350 | 0.0505 | 0.0215 | 0.052096 | [20 empty] | 2500 | 0 | 0 | 0
[10 empty] | 500 | 0.0354 | 0.0207 | 0.040242 | [20 empty] | 3000 | 0 | 0 | 0
ALUMINUM CABLES |  |  |  | COPPER CABLES | [28 empty] | Three Phase kVA | Three Phase kVA | Z% | R% | X%
| CABLE | CABLE | *TOTAL% | CABLE |  | CABLE | *TOTAL% |  |  | 1000 | 0.0177 | 0.0199 | 0.026438 | [20 empty] | updated 17th Feb. 2000 with table 9 of 5413.7
SIZE | (VOLTS) | ( % ) | FLICKER | (VOLTS) |  | ( % ) | FLICKER |  |  | ALUMINUM CABLES OHMS / 1000 FT @90C | [6 empty] | LRC VALUES (updated 31dec1997)
2 | 0 | 0 | 4.6339 | 0 |  | 0 | 0 |  |  |  | ALUMINUM |  |  |  | COPPER |  |  | MOTOR SIZES IN HORSE POWER
1 | 0 | 0 | 4.6339 | 0 |  | 0 | 0 |  |  | SIZE | R@65C | R@90C | X | Z | R@90C | Z | VOLTAGE | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200
1/0 | 0 | 0 | 4.6339 | 0 |  | 0 | 0 |  |  | 2 | 0.31061 | 0.33653 | 0.045 | 0.28216 | 0.2052 | 0.18366 | 208 | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
2/0 | 0 | 0 | 4.6339 | 0 |  | 0 | 0 |  |  | 1 | 0.24432 | 0.26471 | 0.046 | 0.22896 | 0.1623 | 0.15215 | 240 | 64 | 85 | 92 | 106 | 127 | 162 | 232 | 290 | 365 | 435 | 580 | 725 | 1085 | 1450 | 2170
3/0 | 0 | 0 | 4.6339 | 0 |  | 0 | 0 |  |  | 1/0 | 0.19508 | 0.21136 | 0.044 | 0.18762 | 0.1334 | 0.12915 | 480 | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
4/0 | 0 | 0 | 4.6339 | 0 |  | 0 | 0 |  |  | 2/0 | 0.15455 | 0.16745 | 0.043 | 0.15403 | 0.1028 | 0.10554
250 | 0 | 0 | 4.6339 | 0 |  | 0 | 0 |  |  | 3/0 | 0.12197 | 0.13215 | 0.042 | 0.12689 | 0.0825 | 0.089655
350 | 0 | 0 | 4.6339 | 0 |  | 0 | 0 |  |  | 4/0 | 0.098106 | 0.1063 | 0.041 | 0.10684 | 0.0653 | 0.076094
500 | 0 | 0 | 4.6339 | 0 |  | 0 | 0 |  |  | 250 | 0.082765 | 0.089674 | 0.041 | 0.094374 | 0.0552 | 0.068519
750 | 0 | 0 | 4.6339 | 0 |  | 0 | 0 |  |  | 350 | 0.059848 | 0.064844 | 0.04 | 0.075091 | 0.0404 | 0.056758 |  | 3 Phase | Three-Phase Motor (Sized in HP) | [15 empty] | Transformer Data |  | X/R
1000 | 0 | 0 | 4.6339 | 0 |  | 0 | 0 |  |  | 500 | 0.042235 | 0.04576 | 0.039 | 0.060116 | 0.0289 | 0.047471 |  | Trans | 3 | 4.5 | 5 | 6 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 75 | 100 | 150 | 200 | R | X | Ratio | Z%
[10 empty] | 750 | 0.0281 | 0.030446 | 0.038 | 0.047969 | 0.0199 | 0.04006 |  | 45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.0191 | 0.0193 | 1.0105 | 2.715%
[10 empty] | 1000 | 0.0223 | 0.024161 | 0.037 | 0.042594 | 0.0157 | 0.036248 |  | 75 | 0.66522 | 0.88072 | 0.95567 | 1.0962 | 1.3117 | 1.6771 | 2.4079 | 3.0076 | 3.7852 | 4.5066 | 6.0057 | 7.5142 | 11.2432 | 15.019 | 22.4864 | 30.0474 | 0.0172 | 0.0151 | 0.87791 | 2.289%
WITH REDUCED LRC TO 770A OR 50HP |  |  |  | *TOTAL FLICKER = CABLE (%) + XMFR (%) | [13 empty] | 150 | 0.3078 | 0.40751 | 0.44219 | 0.54094 | 0.60693 | 0.776 | 1.1141 | 1.3916 | 1.7514 | 2.0852 | 2.7789 | 3.4768 | 5.2022 | 6.9493 | 10.4045 | 13.903 | 0.0114 | 0.0154 | 1.3509 | 1.916%
[11 empty] | 0.023 | 0.024115 |  | 0.077 | 0.080732 |  |  | 225 | 0.20691 | 0.27393 | 0.29724 | 0.34096 | 0.40798 | 0.52163 | 0.74894 | 0.93544 | 1.1773 | 1.4017 | 1.868 | 2.3372 | 3.497 | 4.6714 | 6.994 | 9.3457 | 0.0119 | 0.0154 | 1.2941 | 1.946%
[18 empty] | 300 | 0.19214 | 0.25438 | 0.27603 | 0.31663 | 0.37887 | 0.48441 | 0.69549 | 0.86869 | 1.0933 | 1.3017 | 1.7347 | 2.1704 | 3.2474 | 4.338 | 6.4949 | 8.6788 | 0.0102 | 0.0205 | 2.0098 | 2.29%
Lookup Value |  | 0 | [15 empty] | 500 | 0.22773 | 0.3015 | 0.32716 | 0.37527 | 0.44904 | 0.57413 | 0.82432 | 1.0296 | 1.2958 | 1.5428 | 2.056 | 2.5724 | 3.8489 | 5.1415 | 7.6979 | 10.2863 | 0.0081 | 0.0443 | 5.4691 | 4.503%
Lookup | Wire | Volatge Drop | % Volatge Drop | SER1 | SER6 | X% | [11 empty] | 750 | 0.20315 | 0.26896 | 0.29185 | 0.33476 | 0.40057 | 0.51216 | 0.73534 | 0.91846 | 1.1559 | 1.3763 | 1.8341 | 2.2947 | 3.4335 | 4.5866 | 6.867 | 9.176 | 0.0095 | 0.0597 | 6.2842 | 6.045%
1 | 2 | 0 | 0 | 0.28216 | 0.28216 | 0.045 | ser 1 | 0 | [9 empty] | 1000 | 0.14663 | 0.19413 | 0.21065 | 0.24163 | 0.28913 | 0.36968 | 0.53076 | 0.66294 | 0.83435 | 0.99337 | 1.3238 | 1.6563 | 2.4783 | 3.3106 | 4.9565 | 6.6232 | 0.009 | 0.0575 | 6.3889 | 5.82%
2 | 1/0 | 0 | 0 | 0.18762 | 0.18762 | 0.044 | ser 6 | 0 | [9 empty] | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
3 | 3/0 | 0 | 0 | 0.12689 | 0.12689 | 0.042 | [11 empty] | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
4 | 350 | 0 | 0 | 0.075091 | 0.075091 | 0.04 | [11 empty] | 2500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
5 | 500 | 0 | 0 | 0.060116 | 0.060116 | 0.039 | [11 empty] | 3000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0%
6 | 1000 | 0 | 0 | [14 empty] | Locked Rotor Current
[18 empty] | @208V | 71 | 94 | 102 | 117 | 140 | 179 | 257 | 321 | 404 | 481 | 641 | 802 | 1200 | 1603 | 2400 | 3207
[18 empty] | @480V | 32 | 43 | 46 | 53 | 63.5 | 81 | 116 | 145 | 183 | 218 | 290 | 363 | 543 | 725 | 1085 | 1450
1 Phase
Trans
(kVA)
25
50
75
100
167
[18 empty] | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE |  |  | Three Phase Motor Data |  | Three PH Motor REF | 9 | HP | #N/A
[18 empty] | 1 | 1 |  |  | 1HP | 0.75 | 41.4096 |  |  | LOOKUP | HP | P.F. | REF
[18 empty] | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096 |  |  | 1 | 3 | 0.3 | 11 | SER 1 | 72.5424
[18 empty] | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096 |  |  | 2 | 4.5 | 0.3 | 14 | SER 2 | 72.5424
[18 empty] | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096 |  |  | 3 | 5 | 0.3 | 9 | SER 3 | 72.5424
[18 empty] | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096 |  |  | 4 | 6 | 0.3 |  | SEC 1 | 72.5424
[18 empty] | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096 |  |  | 5 | 7.5 | 0.3 |  |  | 72.5424
[18 empty] | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096 |  |  | 6 | 10 | 0.3 |  |  | 72.5424
[18 empty] | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096 |  |  | 7 | 15 | 0.3 |  |  | 72.5424
[18 empty] | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096 |  |  | 8 | 20 | 0.3 |  |  | 72.5424
[18 empty] | SINGLE PHASE LOOKUPS |  | Single PH Motor REF |  | 7 | HP | #N/A |  |  | 9 | 25 | 0.3 |  |  | 72.5424
[27 empty] | 10 | 30 | 0.419 |  |  | 65.2285
[27 empty] | 11 | 40 | 0.39 |  |  | 67.0455
[27 empty] | 12 | 50 | 0.382 |  |  | 67.5424
[27 empty] | 13 | 60 | 0.349 |  |  | 69.5738
[27 empty] | 14 | 75 | 0.33 |  |  | 70.7312
[27 empty] | 15 | 100 | 0.309 |  |  | 72.001
[27 empty] | 16 | 150 | 0.28 |  |  | 73.7398
[27 empty] | 17 | 200 | 0.251 |  |  | 75.4633
[27 empty] | 18 | 250 | 0.231 |  |  | 76.644
[27 empty] | 19 | 300 | 0.219 |  |  | 77.3497
[27 empty] | 20 | 400 | 0.199 |  |  | 78.5215
[27 empty] | 21 | 500 | 0.178 |  |  | 79.7467
[27 empty] | 22 | 600 | 0.2 |  |  | 78.463
[27 empty] | 23 | 700 | 0.167 |  |  | 80.3866
[27 empty] | 24 | 800 | 0.167 |  |  | 80.3866
[27 empty] | 25 | 900 | 0.161 |  |  | 80.7351
[27 empty] | 26 | 1000 | 0.048 |  |  | 87.2487
[27 empty] | 27 | 1200 | 0.148 |  |  | 81.489
[27 empty] | 28 | 1500 | 0.148 |  |  | 81.489

## OHVDROP1 (hidden)
Single PH Transformers |  |  | Lookup | 2 |  | Transformer Data |  |  |  |  | Correction Factor |  | 0 | 1
| Ref |  | Value |  | Tranfformer |  | R | X | X/R | Z% | 1.2% | 1.3% | 1.4% | 1.5% | 1.6% | 1.7%
| 1 |  | 10 |  | 10 KVA |  | 1.9% | 0.9% | 0.47368 | 2.102% | bar: 1.2% to 1.7%
| 2 |  | 15 |  | 15 KVA |  | 1.5% | 1.5% | 1 | 2.121% | bar: 1.2% to 1.7%
| 3 |  | 25 |  | 25 KVA |  | 1.4% | 1.4% | 1 | 1.98% | bar: 1.2% to 1.7%
| 4 |  | 37.5 |  | 37.5 KVA |  | 1.4% | 1.6% | 1.1429 | 2.126% | bar: 1.2% to 1.7%
| 5 |  | 50 |  | 50 KVA |  | 1.3% | 1.9% | 1.4615 | 2.302% | [9 empty] | Rt=Ro(1+aT) Ro=R0C | bar: 1.2% to 1.7%
| 6 |  | 75 |  | 75 KVA |  | 1.1% | 1.9% | 1.7273 | 2.195% | [9 empty] | COPPER a=0.004264 | [12 empty] | Transformer | Polemount Transformer Size - kVA | bar: 1.2% to 1.7%
| 7 |  | 100 |  | 100 KVA |  | 1.3% | 2% | 1.5385 | 2.385% | [9 empty] | ALUMINUM a=0.004200 | [12 empty] | Loading | 10 | 15 | 25 | 50 | 75 | 100 | bar: 1.2% to 1.7%
[11 empty] | 1.4%: %Vd =(Vd/Vab)*100 |  | %Vd = (KW/(Vo*cos a))*100*2Z/Vo | [14 empty] | 50% | 1.1 | 1 | 1.05 | 1.1 | 1.05 | 1
[11 empty] | 1.4%: Vd = IZ |  | T@nC=T@25C(234.5+T@nC)/259.5 | [14 empty] | 60% | 1.32 | 1.2 | 1.26 | 1.32 | 1.26 | 1.2
[11 empty] | 1.4%: KW = VIcos a => I = KW/(Vcos a) |  | X@D=X@1FOOT(0.528*LOGV@D-0.57) | [14 empty] | 70% | 1.54 | 1.4 | 1.47 | 1.54 | 1.47 | 1.4
[11 empty] | 1.4%: Z = Rcos a +Xsin a |  | D>1FOOT | [14 empty] | 80% | 1.76 | 1.6 | 1.68 | 1.76 | 1.68 | 1.6
| PF |  | < |  | 1-PH = 1 |  | SYSTEM |  | LOAD KW | [8 empty] | R1/R2=(234.5+T1)/(234.5+T2) | [14 empty] | 90% | 1.98 | 1.8 | 1.89 | 1.98 | 1.89 | 1.8
| 0.9 |  | 25.8419 |  | 3-PH = 3 |  | 1 |  | 0 | [7 empty] | Vd | [15 empty] | 100% | 2.2 | 2 | 2.1 | 2.2 | 2.1 | 2 | bar: 1.6% to 1.7%
[11 empty] | 1.6%: Vab; 1.7%: L | [16 empty] | 110% | 2.42 | 2.2 | 2.31 | 2.42 | 2.31 | 2.2
| VOLTAGE |  |  |  | RUNS |  | LENGTH FT |  | LINE-AMPS | [23 empty] | 120% | 2.64 | 2.4 | 2.52 | 2.64 | 2.52 | 2.4
| 120 |  | 240 |  | 1 |  | 0 |  | 0 | [23 empty] | 130% | 2.86 | 2.6 | 2.73 | 2.86 | 2.73 | 2.6
[33 empty] | 140% | 3.08 | 2.8 | 2.94 | 3.08 | 2.94 | 2.8
| kVA |  |  |  | 15 |  | 0 | Transformer Load kw | [24 empty] | 150% | 3.3 | 3 | 3.15 | 3.3 | 3.15 | 3
| Percentage Load |  |  |  | 0% |  | 1 | Motor Size | [24 empty] | 160% | 3.52 | 3.2 | 3.36 | 3.52 | 3.36 | 3.2
| %Transformer Volt Drop |  |  |  | 0% |  | 1.5% | Transformer %R | [17 empty] | POLYETHYLENE INSULATED ALUMINUM (WEATHERPROOF) | [6 empty] | 170% | 3.74 | 3.4 | 3.57 | 3.74 | 3.57 | 3.4
| %Transformer Flicker Drop |  |  |  | 0.9146% |  | 1.5% | Transformer %X |  |  | 1.6%: CONDUCTOR DATA | [8 empty] | SIZE | 6 | 4 | 2 | 1/0 | 3/0 | 336.4
| POLYETHYLENE INSULATED ALUMINUM (WEATHERPROOF) | [9 empty] | 1.4%: POLYETHYLENE INSULATED ALUMINUM (WEATHERPROOF) OHMS/1000 FEET | [8 empty] | AMPACITY | 95 | 125 | 170 | 230 | 310 | 480
|  |  |  | RACK |  |  |  | XARM | [14 empty] | Flicker
AMPACITY | SIZE |  | V - DROP | FICKER | % DROP | % FLICKER | V - DROP |  | % DROP |  | 1.4%: SIZE; 1.6%: R 25 C | R 75 C | X-RACK |  | X-XARM |  | Z-RACK | Z-RACK F | Z-XARM
OK | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 6; 1.6%: 0.674 | 0.80387 | 0.128 |  | 0.13728 |  | 0.77927 | 0.68756 | 0.78332
OK | 4 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 4; 1.6%: 0.425 | 0.50689 | 0.125 |  | 0.13428 |  | 0.51069 | 0.46285 | 0.51473
OK | 2 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 2; 1.6%: 0.267 | 0.31845 | 0.126 |  | 0.13528 |  | 0.34152 | 0.32217 | 0.34557 |  | POLYETHYLENE INSULATED COPPER (WEATHERPROOF)
OK | 1/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 1/0; 1.6%: 0.168 | 0.20037 | 0.124 |  | 0.13328 |  | 0.23438 | 0.2323 | 0.23843 | SIZE | 6 | 4 | 2 | 1/0 | 2/0
OK | 3/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 3/0; 1.6%: 0.134 | 0.15982 | 0.122 |  | 0.13128 |  | 0.19702 | 0.20056 | 0.20106 | AMPACITY
OK | 336.4 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 336.4; 1.6%: 0.106 | 0.12642 | 0.118 |  | 0.12728 |  | 0.16522 | 0.17287 | 0.16926
| POLYETHYLENE INSULATED COPPER (WEATHERPROOF) | [9 empty] | 1.4%: POLYETHYLENE INSULATED COPPER (WEATHERPROOF) OHMS/1000 FEET
|  |  |  | RACK |  |  |  | XARM
AMPACITY | SIZE |  | V - DROP |  | % DROP |  | V - DROP |  | % DROP |  | 1.4%: SIZE; 1.6%: R 25 C | R 75 C | X-RACK |  | X-XARM |  | Z-RACK |  | Z-XARM |  | RTS REVERSE TWIST SECONDARY ALUMINUM
OK | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 6; 1.6%: 0.419 | 0.49973 | 0.118 |  | 0.12728 |  | 0.50119 |  | 0.50524 | SIZE | 1/0 | 3/0 | 336.4
OK | 4 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 4; 1.6%: 0.2584 | 0.30819 | 0.118 |  | 0.12728 |  | 0.3288 |  | 0.33285 | AMPACITY | 180 | 250 | 400
OK | 2 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 2; 1.6%: 0.1626 | 0.19393 | 0.118 |  | 0.12728 |  | 0.22597 |  | 0.23002
OK | 1/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 1/0; 1.6%: 0.1022 | 0.12189 | 0.118 |  | 0.12728 |  | 0.16114 |  | 0.16518
OK | 2/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 2/0; 1.6%: 0.0811 | 0.096726 | 0.118 |  | 0.12728 |  | 0.13849 |  | 0.14253
[11 empty] | 1.4%: RTS REVERSE TWIST SECONDARY ALUMINUM | [9 empty] | SELF SUPPORTING SECONDARY TRIPLEX OR QUADRUPLEX
|  |  | RTS REVERSE TWIST SECONDARY ALUMINUM | [21 empty] | SIZE | 6 | 4 | 2 | 1/0 | 3/0
AMPACITY |  |  | SIZE | V - DROP | FICKER | % DROP | % FLICKER |  |  |  | 1.4%: SIZE; 1.6%: R 25 C | R 75 C | X |  | Z | Z FICKER |  |  |  | AMPACITY (Tripx) | ------ | 100 | 135 | 180 | ------
|  |  | 2 | 0 | 0 | 0 | 0 |  |  |  | 1.4%: 1/0; 1.6%: 0.1661 | 0.1981 | 0.039205 |  | 0.19538 | 0.17451 |  |  |  | AMPACITY (Quadx) | ------ | ------ | 112 | ------ | 192
|  |  | 1/0 | 0 | 0 | 0 | 0 | 180 |  |  | 1.4%: 3/0; 1.6%: 0.1046 | 0.12475 | 0.036742 |  | 0.12829 | 0.11787
|  |  | 3/0 | 0 | 0 | 0 | 0 | 250 |  |  | 1.4%: 336.4; 1.6%: 0.053 | 0.063212 | 0.0348 |  | 0.07206 | 0.070427
|  |  | 336.4 | 0 | 0 | 0 | 0 | 400
THW COPPER WIRE
[11 empty] | 1.4%: SELF SUPPORTING SECONDARY WITH BARE NEUTRAL MESSENGER | [8 empty] | SIZE | 6 | 4 | 2 | 1/0 | 2/0 | 3/0 | 4/0 | 500
| SELF SUPPORTING SECONDARY TRIPLEX OR QUADRUPLEX | [23 empty] | AMPACITY | 96 | 125 | 170 | 230 | 265 | 310 | 360
|  |  | ALUMINUM |  |  |  | COPPER |  |  |  | 1.4%: ALUMINUM |  |  |  | COPPER
AMPACITY | SIZE |  | V - DROP | FICKER | % DROP | % FLICKER | V - DROP | FICKER | % DROP | % FLICKER | 1.6%: R 75 C | X | Z | Z Flicker | R 75 C |  | Z | Z FLICKER
| 6 |  | ---- | ---- | ---- | ---- | 0 | 0 | 0 | 0 | 1.4%: 6 | 0.0489 |  |  | 0.4932 |  | 0.4652 | 0.40224
| 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4%: 4; 1.6%: 0.505 | 0.0466 | 0.47481 | 0.40957 | 0.3092 |  | 0.29859 | 0.26272
| 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4%: 2; 1.6%: 0.321 | 0.0434 | 0.30782 | 0.26946 | 0.1957 |  | 0.19505 | 0.17548 |  |  | OPEN COPPER WIRE BARE
| 1/0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 1.4%: 1/0; 1.6%: 0.2016 | 0.0392 | 0.19853 | 0.17713 | [5 empty] | SIZE | 6/1 | 6/3 | 4/1 | 4/3 | 2 | 1/0 | 2/0 | 3/0 | 4/0 | 500
| 3/0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 1.4%: 3/0; 1.6%: 0.126 | 0.0367 | 0.1294 | 0.11877 | [5 empty] | AMPACITY
|  |  |  | THW COPPER WIRE | [6 empty] | 1.7%: THW COPPER WIRE AND TREE WIRE
|  |  |  | RACK |  |  |  | XARM
AMPACITY | SIZE |  | V - DROP |  | % DROP |  | V - DROP |  | % DROP |  | 1.6%: R 75 C | X-RACK | X-XARM |  | Z-RACK |  | Z-XARM
| 6 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 6; 1.6%: 0.4932 | 0.0867 | 0.095978 |  | 0.48167 |  | 0.48572
| 4 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 4; 1.6%: 0.3092 | 0.0813 | 0.090578 |  | 0.31372 |  | 0.31776
| 2 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 2; 1.6%: 0.1957 | 0.0754 | 0.084678 |  | 0.209 |  | 0.21304
| 1/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 1/0; 1.6%: 0.1282 | 0.0684 | 0.077678 |  | 0.14519 |  | 0.14924
| 2/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 2/0; 1.6%: 0.0981 | 0.0652 | 0.074478 |  | 0.11671 |  | 0.12075
| 3/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 3/0; 1.6%: 0.0787 | 0.0625 | 0.071778 |  | 0.098073 |  | 0.10212
| 4/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 4/0; 1.6%: 0.0622 | 0.0589 | 0.068178 |  | 0.081654 |  | 0.085698
| 500 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 500; 1.6%: 0.0276 | 0.0458 | 0.055078 |  | 0.044804 |  | 0.048848
OPEN COPPER WIRE BARE
|  |  |  | RACK |  |  |  | XARM |  |  | 1.4%: COPPER OPEN WIRE OHMS / 1000 FT
AMPACITY | SIZE |  | V - DROP |  | % DROP |  | V - DROP |  | % DROP |  | 1.4%: SIZE; 1.6%: R 75 C | X-RACK | X-XARM |  | Z-RACK |  | Z-XARM
| 6/1 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 6/1; 1.6%: 0.4925 | 0.1206 | 0.12988 |  | 0.49582 |  | 0.49986
| 6/3 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 6/3; 1.6%: 0.4993 | 0.1185 | 0.12778 |  | 0.50102 |  | 0.50507
| 4/1 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 4/1; 1.6%: 0.3103 | 0.1153 | 0.12458 |  | 0.32953 |  | 0.33357
| 4/3 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 4/3; 1.6%: 0.3136 | 0.1134 | 0.12268 |  | 0.33167 |  | 0.33571
| 2 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 2; 1.6%: 0.1992 | 0.1087 | 0.11798 |  | 0.22666 |  | 0.23071
| 1/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 1/0; 1.6%: 0.1254 | 0.1034 | 0.11268 |  | 0.15793 |  | 0.16198
| 2/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 2/0; 1.6%: 0.0994 | 0.1008 | 0.11008 |  | 0.1334 |  | 0.13744
| 3/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 3/0; 1.6%: 0.0791 | 0.0956 | 0.10488 |  | 0.11286 |  | 0.11691
| 4/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 4/0; 1.6%: 0.0629 | 0.0941 | 0.10338 |  | 0.097627 |  | 0.10167
| 500 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 500; 1.6%: 0.0271 | 0.0843 | 0.093578 |  | 0.061136 |  | 0.06518
[6 empty] | DROP | AMP CHK | FLICKER | Ampacity
|  |  | WIRE REF | 1 |  | 0 | OK | 0 | 100
|  | 1 | #6 CU | OK | 0 | 1 |  | 0 | 100
|  | 2 | #4 AL | OK | 0 | 1 |  | 0 | 100
|  | 3 | #4 CU | OK | 0 | 1 |  | 0 | 135
|  | 4 | #2 AL | OK | 0 | 1 |  | 0 | 135
|  | 5 | #2 CU | OK | 0 | 1 |  | 0 | 180
|  | 6 | 1/0 AL | OK | 0 | 1 |  | 0 | 180
|  | 7 | 3/0 AL | OK | 0 | 1 |  | 0 | 250
|  | 8 | 336.4 AL | OK | 0 | 1 |  | 0 | 400
|  | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE | LCR @ 240 |  | 1.3%: OLD 98 VALUES
|  | 1 | 1 |  |  | 1HP | 0.75 | 41.4096 | 27 |  | 1.3%: 48
|  | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096 | 34 |  | 1.3%: 60
|  | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096 | 46 |  | 1.3%: 72
|  | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096 | 69 |  | 1.3%: 102
|  | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096 | 103 |  | 1.3%: 135
|  | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096 | 115 |  | 1.3%: 168
|  | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096 | 140 |  | 1.3%: 197
|  | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096 | 175 |  | 1.3%: 240
|  | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096 | 218 |  | 1.3%: 300
|  | SINGLE PHASE LOOKUPS |  | Single PH Motor REF |  | 1 |  | LRC | 27
[6 empty] | 1 |  | P.F. | 0.75
[8 empty] | ANGLE | 41.4096
LRC VALUES (updated 5 FEB 1998)
SINGLE-PHASE MOTOR SIZES IN HP
|  | VOLTAGE | 1 | 1.5 | 2
|  | 120 | 46 | 69 | 92
LRC VALUES (updated 5 FEB 1998)
SINGLE-PHASE MOTOR SIZES IN HORSE POWER | bar: 1.2%
|  | VOLTAGE | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 1.2%: 10
|  | 240 | 27 | 34 | 46 | 69 | 103 | 115 | 140 | 175 | 1.2%: 218

## OHVDROP2 (hidden)
Single PH Transformers |  |  | Lookup | 2 |  | Transformer Data |  |  |  |  | Correction Factor |  | 0 | 1
| Ref |  | Value |  | Tranfformer |  | R | X | X/R | Z% | 1.2% | 1.3% | 1.4% | 1.5% | 1.6% | 1.7%
| 1 |  | 10 |  | 10 KVA |  | 1.9% | 0.9% | 0.47368 | 2.102% | bar: 1.2% to 1.7%
| 2 |  | 15 |  | 15 KVA |  | 1.5% | 1.5% | 1 | 2.121% | bar: 1.2% to 1.7%
| 3 |  | 25 |  | 25 KVA |  | 1.4% | 1.4% | 1 | 1.98% | bar: 1.2% to 1.7%
| 4 |  | 37.5 |  | 37.5 KVA |  | 1.4% | 1.6% | 1.1429 | 2.126% | bar: 1.2% to 1.7%
| 5 |  | 50 |  | 50 KVA |  | 1.3% | 1.9% | 1.4615 | 2.302% | [9 empty] | Rt=Ro(1+aT) Ro=R0C | bar: 1.2% to 1.7%
| 6 |  | 75 |  | 75 KVA |  | 1.1% | 1.9% | 1.7273 | 2.195% | [9 empty] | COPPER a=0.004264 | [12 empty] | Transformer | Polemount Transformer Size - kVA | bar: 1.2% to 1.7%
| 7 |  | 100 |  | 100 KVA |  | 1.3% | 2% | 1.5385 | 2.385% | [9 empty] | ALUMINUM a=0.004200 | [12 empty] | Loading | 10 | 15 | 25 | 50 | 75 | 100 | bar: 1.2% to 1.7%
[11 empty] | 1.4%: %Vd =(Vd/Vab)*100 |  | %Vd = (KW/(Vo*cos a))*100*2Z/Vo | [14 empty] | 50% | 1.1 | 1 | 1.05 | 1.1 | 1.05 | 1
[11 empty] | 1.4%: Vd = IZ |  | T@nC=T@25C(234.5+T@nC)/259.5 | [14 empty] | 60% | 1.32 | 1.2 | 1.26 | 1.32 | 1.26 | 1.2
[11 empty] | 1.4%: KW = VIcos a => I = KW/(Vcos a) |  | X@D=X@1FOOT(0.528*LOGV@D-0.57) | [14 empty] | 70% | 1.54 | 1.4 | 1.47 | 1.54 | 1.47 | 1.4
[11 empty] | 1.4%: Z = Rcos a +Xsin a |  | D>1FOOT | [14 empty] | 80% | 1.76 | 1.6 | 1.68 | 1.76 | 1.68 | 1.6
| PF |  | < |  | 1-PH = 1 |  | SYSTEM |  | LOAD KW | [8 empty] | R1/R2=(234.5+T1)/(234.5+T2) | [14 empty] | 90% | 1.98 | 1.8 | 1.89 | 1.98 | 1.89 | 1.8
| 0.9 |  | 25.8419 |  | 3-PH = 3 |  | 1 |  | 0 | [7 empty] | Vd | [15 empty] | 100% | 2.2 | 2 | 2.1 | 2.2 | 2.1 | 2 | bar: 1.6% to 1.7%
[11 empty] | 1.6%: Vab; 1.7%: L | [16 empty] | 110% | 2.42 | 2.2 | 2.31 | 2.42 | 2.31 | 2.2
| VOLTAGE |  |  |  | RUNS |  | LENGTH FT |  | LINE-AMPS | [23 empty] | 120% | 2.64 | 2.4 | 2.52 | 2.64 | 2.52 | 2.4
| 120 |  | 240 |  | 1 |  | 0 |  | 0 | [23 empty] | 130% | 2.86 | 2.6 | 2.73 | 2.86 | 2.73 | 2.6
[33 empty] | 140% | 3.08 | 2.8 | 2.94 | 3.08 | 2.94 | 2.8
| kVA |  |  |  | 15 |  | 0 | Transformer Load kw | [24 empty] | 150% | 3.3 | 3 | 3.15 | 3.3 | 3.15 | 3
| Percentage Load |  |  |  | 0% |  | 1 | Motor Size | [24 empty] | 160% | 3.52 | 3.2 | 3.36 | 3.52 | 3.36 | 3.2
| %Transformer Volt Drop |  |  |  | 0% |  | 1.5% | Transformer %R | [17 empty] | POLYETHYLENE INSULATED ALUMINUM (WEATHERPROOF) | [6 empty] | 170% | 3.74 | 3.4 | 3.57 | 3.74 | 3.57 | 3.4
| %Transformer Flicker Drop |  |  |  | 0.9146% |  | 1.5% | Transformer %X |  |  | 1.6%: CONDUCTOR DATA | [8 empty] | SIZE | 6 | 4 | 2 | 1/0 | 3/0 | 336.4
| POLYETHYLENE INSULATED ALUMINUM (WEATHERPROOF) | [9 empty] | 1.4%: POLYETHYLENE INSULATED ALUMINUM (WEATHERPROOF) OHMS/1000 FEET | [8 empty] | AMPACITY | 95 | 125 | 170 | 230 | 310 | 480
|  |  |  | RACK |  |  |  | XARM
AMPACITY | SIZE |  | V - DROP | FICKER | % DROP | % FLICKER | V - DROP |  | % DROP |  | 1.4%: SIZE; 1.6%: R 25 C | R 75 C | X-RACK |  | X-XARM |  | Z-RACK | Z-RACK F | Z-XARM
OK | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 6; 1.6%: 0.674 | 0.80387 | 0.128 |  | 0.13728 |  | 0.77927 | 0.68756 | 0.78332
OK | 4 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 4; 1.6%: 0.425 | 0.50689 | 0.125 |  | 0.13428 |  | 0.51069 | 0.46285 | 0.51473
OK | 2 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 2; 1.6%: 0.267 | 0.31845 | 0.126 |  | 0.13528 |  | 0.34152 | 0.32217 | 0.34557 |  | POLYETHYLENE INSULATED COPPER (WEATHERPROOF)
OK | 1/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 1/0; 1.6%: 0.168 | 0.20037 | 0.124 |  | 0.13328 |  | 0.23438 | 0.2323 | 0.23843 | SIZE | 6 | 4 | 2 | 1/0 | 2/0
OK | 3/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 3/0; 1.6%: 0.134 | 0.15982 | 0.122 |  | 0.13128 |  | 0.19702 | 0.20056 | 0.20106 | AMPACITY
OK | 336.4 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 336.4; 1.6%: 0.106 | 0.12642 | 0.118 |  | 0.12728 |  | 0.16522 | 0.17287 | 0.16926
| POLYETHYLENE INSULATED COPPER (WEATHERPROOF) | [9 empty] | 1.4%: POLYETHYLENE INSULATED COPPER (WEATHERPROOF) OHMS/1000 FEET
|  |  |  | RACK |  |  |  | XARM
AMPACITY | SIZE |  | V - DROP |  | % DROP |  | V - DROP |  | % DROP |  | 1.4%: SIZE; 1.6%: R 25 C | R 75 C | X-RACK |  | X-XARM |  | Z-RACK |  | Z-XARM |  | RTS REVERSE TWIST SECONDARY ALUMINUM
OK | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 6; 1.6%: 0.419 | 0.49973 | 0.118 |  | 0.12728 |  | 0.50119 |  | 0.50524 | SIZE | 1/0 | 3/0 | 336.4
OK | 4 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 4; 1.6%: 0.2584 | 0.30819 | 0.118 |  | 0.12728 |  | 0.3288 |  | 0.33285 | AMPACITY | 180 | 250 | 400
OK | 2 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 2; 1.6%: 0.1626 | 0.19393 | 0.118 |  | 0.12728 |  | 0.22597 |  | 0.23002
OK | 1/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 1/0; 1.6%: 0.1022 | 0.12189 | 0.118 |  | 0.12728 |  | 0.16114 |  | 0.16518
OK | 2/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 2/0; 1.6%: 0.0811 | 0.096726 | 0.118 |  | 0.12728 |  | 0.13849 |  | 0.14253
[11 empty] | 1.4%: RTS REVERSE TWIST SECONDARY ALUMINUM | [9 empty] | SELF SUPPORTING SECONDARY TRIPLEX OR QUADRUPLEX
|  |  | RTS REVERSE TWIST SECONDARY ALUMINUM | [21 empty] | SIZE | 6 | 4 | 2 | 1/0 | 3/0
AMPACITY |  |  | SIZE | V - DROP | FICKER | % DROP | % FLICKER |  |  |  | 1.4%: SIZE; 1.6%: R 25 C | R 75 C | X |  | Z | Z FICKER |  |  |  | AMPACITY (Tripx) | ------ | 100 | 135 | 180 | ------
|  |  | 2 | 0 | 0 | 0 | 0 |  |  |  | 1.4%: 1/0; 1.6%: 0.1661 | 0.1981 | 0.039205 |  | 0.19538 | 0.17451 |  |  |  | AMPACITY (Quadx) | ------ | ------ | 112 | ------ | 192
|  |  | 1/0 | 0 | 0 | 0 | 0 | 180 |  |  | 1.4%: 3/0; 1.6%: 0.1046 | 0.12475 | 0.036742 |  | 0.12829 | 0.11787
|  |  | 3/0 | 0 | 0 | 0 | 0 | 250 |  |  | 1.4%: 336.4; 1.6%: 0.053 | 0.063212 | 0.0348 |  | 0.07206 | 0.070427
|  |  | 336.4 | 0 | 0 | 0 | 0 | 400
THW COPPER WIRE
[11 empty] | 1.4%: SELF SUPPORTING SECONDARY WITH BARE NEUTRAL MESSENGER | [8 empty] | SIZE | 6 | 4 | 2 | 1/0 | 2/0 | 3/0 | 4/0 | 500
| SELF SUPPORTING SECONDARY TRIPLEX OR QUADRUPLEX | [23 empty] | AMPACITY | 96 | 125 | 170 | 230 | 265 | 310 | 360
|  |  | ALUMINUM |  |  |  | COPPER |  |  |  | 1.4%: ALUMINUM |  |  |  | COPPER
AMPACITY | SIZE |  | V - DROP | FICKER | % DROP | % FLICKER | V - DROP | FICKER | % DROP | % FLICKER | 1.6%: R 75 C | X | Z | Z Flicker | R 75 C |  | Z | Z FLICKER
| 6 |  | ---- | ---- | ---- | ---- | 0 | 0 | 0 | 0 | 1.4%: 6 | 0.0489 |  |  | 0.4932 |  | 0.4652 | 0.40224
| 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4%: 4; 1.6%: 0.505 | 0.0466 | 0.47481 | 0.40957 | 0.3092 |  | 0.29859 | 0.26272
| 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4%: 2; 1.6%: 0.321 | 0.0434 | 0.30782 | 0.26946 | 0.1957 |  | 0.19505 | 0.17548 |  |  | OPEN COPPER WIRE BARE
| 1/0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 1.4%: 1/0; 1.6%: 0.2016 | 0.0392 | 0.19853 | 0.17713 | [5 empty] | SIZE | 6/1 | 6/3 | 4/1 | 4/3 | 2 | 1/0 | 2/0 | 3/0 | 4/0 | 500
| 3/0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 1.4%: 3/0; 1.6%: 0.126 | 0.0367 | 0.1294 | 0.11877 | [5 empty] | AMPACITY
|  |  |  | THW COPPER WIRE | [6 empty] | 1.7%: THW COPPER WIRE AND TREE WIRE
|  |  |  | RACK |  |  |  | XARM
AMPACITY | SIZE |  | V - DROP |  | % DROP |  | V - DROP |  | % DROP |  | 1.6%: R 75 C | X-RACK | X-XARM |  | Z-RACK |  | Z-XARM
| 6 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 6; 1.6%: 0.4932 | 0.0867 | 0.095978 |  | 0.48167 |  | 0.48572
| 4 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 4; 1.6%: 0.3092 | 0.0813 | 0.090578 |  | 0.31372 |  | 0.31776
| 2 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 2; 1.6%: 0.1957 | 0.0754 | 0.084678 |  | 0.209 |  | 0.21304
| 1/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 1/0; 1.6%: 0.1282 | 0.0684 | 0.077678 |  | 0.14519 |  | 0.14924
| 2/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 2/0; 1.6%: 0.0981 | 0.0652 | 0.074478 |  | 0.11671 |  | 0.12075
| 3/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 3/0; 1.6%: 0.0787 | 0.0625 | 0.071778 |  | 0.098073 |  | 0.10212
| 4/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 4/0; 1.6%: 0.0622 | 0.0589 | 0.068178 |  | 0.081654 |  | 0.085698
| 500 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 500; 1.6%: 0.0276 | 0.0458 | 0.055078 |  | 0.044804 |  | 0.048848
OPEN COPPER WIRE BARE
|  |  |  | RACK |  |  |  | XARM |  |  | 1.4%: COPPER OPEN WIRE OHMS / 1000 FT
AMPACITY | SIZE |  | V - DROP |  | % DROP |  | V - DROP |  | % DROP |  | 1.4%: SIZE; 1.6%: R 75 C | X-RACK | X-XARM |  | Z-RACK |  | Z-XARM
| 6/1 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 6/1; 1.6%: 0.4925 | 0.1206 | 0.12988 |  | 0.49582 |  | 0.49986
| 6/3 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 6/3; 1.6%: 0.4993 | 0.1185 | 0.12778 |  | 0.50102 |  | 0.50507
| 4/1 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 4/1; 1.6%: 0.3103 | 0.1153 | 0.12458 |  | 0.32953 |  | 0.33357
| 4/3 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 4/3; 1.6%: 0.3136 | 0.1134 | 0.12268 |  | 0.33167 |  | 0.33571
| 2 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 2; 1.6%: 0.1992 | 0.1087 | 0.11798 |  | 0.22666 |  | 0.23071
| 1/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 1/0; 1.6%: 0.1254 | 0.1034 | 0.11268 |  | 0.15793 |  | 0.16198
| 2/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 2/0; 1.6%: 0.0994 | 0.1008 | 0.11008 |  | 0.1334 |  | 0.13744
| 3/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 3/0; 1.6%: 0.0791 | 0.0956 | 0.10488 |  | 0.11286 |  | 0.11691
| 4/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 4/0; 1.6%: 0.0629 | 0.0941 | 0.10338 |  | 0.097627 |  | 0.10167
| 500 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 500; 1.6%: 0.0271 | 0.0843 | 0.093578 |  | 0.061136 |  | 0.06518
[6 empty] | DROP | AMP CHK | FLICKER | Ampacity
|  |  | WIRE REF | 1 |  | 0 | OK | 0 | 100
|  | 1 | #6 CU | OK | 0 | 1 |  | 0 | 100
|  | 2 | #4 AL | OK | 0 | 1 |  | 0 | 100
|  | 3 | #4 CU | OK | 0 | 1 |  | 0 | 135
|  | 4 | #2 AL | OK | 0 | 1 |  | 0 | 135
|  | 5 | #2 CU | OK | 0 | 1 |  | 0 | 180
|  | 6 | 1/0 AL | OK | 0 | 1 |  | 0 | 180
|  | 7 | 3/0 AL | OK | 0 | 1 |  | 0 | 250
|  | 8 | 336.4 AL | OK | 0 | 1 |  | 0 | 400
|  | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE | LCR @ 240 |  | 1.3%: OLD 98 VALUES
|  | 1 | 1 |  |  | 1HP | 0.75 | 41.4096 | 27 |  | 1.3%: 48
|  | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096 | 34 |  | 1.3%: 60
|  | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096 | 46 |  | 1.3%: 72
|  | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096 | 69 |  | 1.3%: 102
|  | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096 | 103 |  | 1.3%: 135
|  | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096 | 115 |  | 1.3%: 168
|  | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096 | 140 |  | 1.3%: 197
|  | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096 | 175 |  | 1.3%: 240
|  | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096 | 218 |  | 1.3%: 300
|  | SINGLE PHASE LOOKUPS |  | Single PH Motor REF |  | 1 |  | LRC | 27
[6 empty] | 1 |  | P.F. | 0.75
[8 empty] | ANGLE | 41.4096
LRC VALUES (updated 5 FEB 1998)
SINGLE-PHASE MOTOR SIZES IN HP
|  | VOLTAGE | 1 | 1.5 | 2
|  | 120 | 46 | 69 | 92
LRC VALUES (updated 5 FEB 1998)
SINGLE-PHASE MOTOR SIZES IN HORSE POWER | bar: 1.2%
|  | VOLTAGE | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 1.2%: 10
|  | 240 | 27 | 34 | 46 | 69 | 103 | 115 | 140 | 175 | 1.2%: 218

## OHVDROP3 (hidden)
Single PH Transformers |  |  | Lookup | 2 |  | Transformer Data |  |  |  |  | Correction Factor |  | 0 | 1
| Ref |  | Value |  | Tranfformer |  | R | X | X/R | Z% | 1.2% | 1.3% | 1.4% | 1.5% | 1.6% | 1.7%
| 1 |  | 10 |  | 10 KVA |  | 1.9% | 0.9% | 0.47368 | 2.102% | bar: 1.2% to 1.7%
| 2 |  | 15 |  | 15 KVA |  | 1.5% | 1.5% | 1 | 2.121% | bar: 1.2% to 1.7%
| 3 |  | 25 |  | 25 KVA |  | 1.4% | 1.4% | 1 | 1.98% | bar: 1.2% to 1.7%
| 4 |  | 37.5 |  | 37.5 KVA |  | 1.4% | 1.6% | 1.1429 | 2.126% | bar: 1.2% to 1.7%
| 5 |  | 50 |  | 50 KVA |  | 1.3% | 1.9% | 1.4615 | 2.302% | [9 empty] | Rt=Ro(1+aT) Ro=R0C | bar: 1.2% to 1.7%
| 6 |  | 75 |  | 75 KVA |  | 1.1% | 1.9% | 1.7273 | 2.195% | [9 empty] | COPPER a=0.004264 | [12 empty] | Transformer | Polemount Transformer Size - kVA | bar: 1.2% to 1.7%
| 7 |  | 100 |  | 100 KVA |  | 1.3% | 2% | 1.5385 | 2.385% | [9 empty] | ALUMINUM a=0.004200 | [12 empty] | Loading | 10 | 15 | 25 | 50 | 75 | 100 | bar: 1.2% to 1.7%
[11 empty] | 1.4%: %Vd =(Vd/Vab)*100 |  | %Vd = (KW/(Vo*cos a))*100*2Z/Vo | [14 empty] | 50% | 1.1 | 1 | 1.05 | 1.1 | 1.05 | 1
[11 empty] | 1.4%: Vd = IZ |  | T@nC=T@25C(234.5+T@nC)/259.5 | [14 empty] | 60% | 1.32 | 1.2 | 1.26 | 1.32 | 1.26 | 1.2
[11 empty] | 1.4%: KW = VIcos a => I = KW/(Vcos a) |  | X@D=X@1FOOT(0.528*LOGV@D-0.57) | [14 empty] | 70% | 1.54 | 1.4 | 1.47 | 1.54 | 1.47 | 1.4
[11 empty] | 1.4%: Z = Rcos a +Xsin a |  | D>1FOOT | [14 empty] | 80% | 1.76 | 1.6 | 1.68 | 1.76 | 1.68 | 1.6
| PF |  | < |  | 1-PH = 1 |  | SYSTEM |  | LOAD KW | [8 empty] | R1/R2=(234.5+T1)/(234.5+T2) | [14 empty] | 90% | 1.98 | 1.8 | 1.89 | 1.98 | 1.89 | 1.8
| 0.9 |  | 25.8419 |  | 3-PH = 3 |  | 1 |  | 0 | [7 empty] | Vd | [15 empty] | 100% | 2.2 | 2 | 2.1 | 2.2 | 2.1 | 2 | bar: 1.6% to 1.7%
[11 empty] | 1.6%: Vab; 1.7%: L | [16 empty] | 110% | 2.42 | 2.2 | 2.31 | 2.42 | 2.31 | 2.2
| VOLTAGE |  |  |  | RUNS |  | LENGTH FT |  | LINE-AMPS | [23 empty] | 120% | 2.64 | 2.4 | 2.52 | 2.64 | 2.52 | 2.4
| 120 |  | 240 |  | 1 |  | 0 |  | 0 | [23 empty] | 130% | 2.86 | 2.6 | 2.73 | 2.86 | 2.73 | 2.6
[33 empty] | 140% | 3.08 | 2.8 | 2.94 | 3.08 | 2.94 | 2.8
| kVA |  |  |  | 15 |  | 0 | Transformer Load kw | [24 empty] | 150% | 3.3 | 3 | 3.15 | 3.3 | 3.15 | 3
| Percentage Load |  |  |  | 0% |  | 5 | Motor Size | [24 empty] | 160% | 3.52 | 3.2 | 3.36 | 3.52 | 3.36 | 3.2
| %Transformer Volt Drop |  |  |  | 0% |  | 1.5% | Transformer %R | [17 empty] | POLYETHYLENE INSULATED ALUMINUM (WEATHERPROOF) | [6 empty] | 170% | 3.74 | 3.4 | 3.57 | 3.74 | 3.57 | 3.4
| %Transformer Flicker Drop |  |  |  | 3.896% |  | 1.5% | Transformer %X |  |  | 1.6%: CONDUCTOR DATA | [8 empty] | SIZE | 6 | 4 | 2 | 1/0 | 3/0 | 336.4
| POLYETHYLENE INSULATED ALUMINUM (WEATHERPROOF) | [9 empty] | 1.4%: POLYETHYLENE INSULATED ALUMINUM (WEATHERPROOF) OHMS/1000 FEET | [8 empty] | AMPACITY | 95 | 125 | 170 | 230 | 310 | 480
|  |  |  | RACK |  |  |  | XARM
AMPACITY | SIZE |  | V - DROP | FICKER | % DROP | % FLICKER | V - DROP |  | % DROP |  | 1.4%: SIZE; 1.6%: R 25 C | R 75 C | X-RACK |  | X-XARM |  | Z-RACK | Z-RACK F | Z-XARM
OK | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 6; 1.6%: 0.674 | 0.80387 | 0.128 |  | 0.13728 |  | 0.77927 | 0.68756 | 0.78332
OK | 4 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 4; 1.6%: 0.425 | 0.50689 | 0.125 |  | 0.13428 |  | 0.51069 | 0.46285 | 0.51473
OK | 2 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 2; 1.6%: 0.267 | 0.31845 | 0.126 |  | 0.13528 |  | 0.34152 | 0.32217 | 0.34557 |  | POLYETHYLENE INSULATED COPPER (WEATHERPROOF)
OK | 1/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 1/0; 1.6%: 0.168 | 0.20037 | 0.124 |  | 0.13328 |  | 0.23438 | 0.2323 | 0.23843 | SIZE | 6 | 4 | 2 | 1/0 | 2/0
OK | 3/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 3/0; 1.6%: 0.134 | 0.15982 | 0.122 |  | 0.13128 |  | 0.19702 | 0.20056 | 0.20106 | AMPACITY
OK | 336.4 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 336.4; 1.6%: 0.106 | 0.12642 | 0.118 |  | 0.12728 |  | 0.16522 | 0.17287 | 0.16926
| POLYETHYLENE INSULATED COPPER (WEATHERPROOF) | [9 empty] | 1.4%: POLYETHYLENE INSULATED COPPER (WEATHERPROOF) OHMS/1000 FEET
|  |  |  | RACK |  |  |  | XARM
AMPACITY | SIZE |  | V - DROP |  | % DROP |  | V - DROP |  | % DROP |  | 1.4%: SIZE; 1.6%: R 25 C | R 75 C | X-RACK |  | X-XARM |  | Z-RACK |  | Z-XARM |  | RTS REVERSE TWIST SECONDARY ALUMINUM
OK | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 6; 1.6%: 0.419 | 0.49973 | 0.118 |  | 0.12728 |  | 0.50119 |  | 0.50524 | SIZE | 1/0 | 3/0 | 336.4
OK | 4 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 4; 1.6%: 0.2584 | 0.30819 | 0.118 |  | 0.12728 |  | 0.3288 |  | 0.33285 | AMPACITY | 180 | 250 | 400
OK | 2 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 2; 1.6%: 0.1626 | 0.19393 | 0.118 |  | 0.12728 |  | 0.22597 |  | 0.23002
OK | 1/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 1/0; 1.6%: 0.1022 | 0.12189 | 0.118 |  | 0.12728 |  | 0.16114 |  | 0.16518
OK | 2/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 2/0; 1.6%: 0.0811 | 0.096726 | 0.118 |  | 0.12728 |  | 0.13849 |  | 0.14253
[11 empty] | 1.4%: RTS REVERSE TWIST SECONDARY ALUMINUM | [9 empty] | SELF SUPPORTING SECONDARY TRIPLEX OR QUADRUPLEX
|  |  | RTS REVERSE TWIST SECONDARY ALUMINUM | [21 empty] | SIZE | 6 | 4 | 2 | 1/0 | 3/0
AMPACITY |  |  | SIZE | V - DROP | FICKER | % DROP | % FLICKER |  |  |  | 1.4%: SIZE; 1.6%: R 25 C | R 75 C | X |  | Z | Z FICKER |  |  |  | AMPACITY (Tripx) | ------ | 100 | 135 | 180 | ------
|  |  | 2 | 0 | 0 | 0 | 0 |  |  |  | 1.4%: 1/0; 1.6%: 0.1661 | 0.1981 | 0.039205 |  | 0.19538 | 0.17451 |  |  |  | AMPACITY (Quadx) | ------ | ------ | 112 | ------ | 192
|  |  | 1/0 | 0 | 0 | 0 | 0 | 180 |  |  | 1.4%: 3/0; 1.6%: 0.1046 | 0.12475 | 0.036742 |  | 0.12829 | 0.11787
|  |  | 3/0 | 0 | 0 | 0 | 0 | 250 |  |  | 1.4%: 336.4; 1.6%: 0.053 | 0.063212 | 0.0348 |  | 0.07206 | 0.070427
|  |  | 336.4 | 0 | 0 | 0 | 0 | 400
THW COPPER WIRE
[11 empty] | 1.4%: SELF SUPPORTING SECONDARY WITH BARE NEUTRAL MESSENGER | [8 empty] | SIZE | 6 | 4 | 2 | 1/0 | 2/0 | 3/0 | 4/0 | 500
| SELF SUPPORTING SECONDARY TRIPLEX OR QUADRUPLEX | [23 empty] | AMPACITY | 96 | 125 | 170 | 230 | 265 | 310 | 360
|  |  | ALUMINUM |  |  |  | COPPER |  |  |  | 1.4%: ALUMINUM |  |  |  | COPPER
AMPACITY | SIZE |  | V - DROP | FICKER | % DROP | % FLICKER | V - DROP | FICKER | % DROP | % FLICKER | 1.6%: R 75 C | X | Z | Z Flicker | R 75 C |  | Z | Z FLICKER
| 6 |  | ---- | ---- | ---- | ---- | 0 | 0 | 0 | 0 | 1.4%: 6 | 0.0489 |  |  | 0.4932 |  | 0.4652 | 0.40224
| 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4%: 4; 1.6%: 0.505 | 0.0466 | 0.47481 | 0.40957 | 0.3092 |  | 0.29859 | 0.26272
| 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4%: 2; 1.6%: 0.321 | 0.0434 | 0.30782 | 0.26946 | 0.1957 |  | 0.19505 | 0.17548 |  |  | OPEN COPPER WIRE BARE
| 1/0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 1.4%: 1/0; 1.6%: 0.2016 | 0.0392 | 0.19853 | 0.17713 | [5 empty] | SIZE | 6/1 | 6/3 | 4/1 | 4/3 | 2 | 1/0 | 2/0 | 3/0 | 4/0 | 500
| 3/0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 1.4%: 3/0; 1.6%: 0.126 | 0.0367 | 0.1294 | 0.11877 | [5 empty] | AMPACITY
|  |  |  | THW COPPER WIRE | [6 empty] | 1.7%: THW COPPER WIRE AND TREE WIRE
|  |  |  | RACK |  |  |  | XARM
AMPACITY | SIZE |  | V - DROP |  | % DROP |  | V - DROP |  | % DROP |  | 1.6%: R 75 C | X-RACK | X-XARM |  | Z-RACK |  | Z-XARM
| 6 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 6; 1.6%: 0.4932 | 0.0867 | 0.095978 |  | 0.48167 |  | 0.48572
| 4 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 4; 1.6%: 0.3092 | 0.0813 | 0.090578 |  | 0.31372 |  | 0.31776
| 2 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 2; 1.6%: 0.1957 | 0.0754 | 0.084678 |  | 0.209 |  | 0.21304
| 1/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 1/0; 1.6%: 0.1282 | 0.0684 | 0.077678 |  | 0.14519 |  | 0.14924
| 2/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 2/0; 1.6%: 0.0981 | 0.0652 | 0.074478 |  | 0.11671 |  | 0.12075
| 3/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 3/0; 1.6%: 0.0787 | 0.0625 | 0.071778 |  | 0.098073 |  | 0.10212
| 4/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 4/0; 1.6%: 0.0622 | 0.0589 | 0.068178 |  | 0.081654 |  | 0.085698
| 500 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 500; 1.6%: 0.0276 | 0.0458 | 0.055078 |  | 0.044804 |  | 0.048848
OPEN COPPER WIRE BARE
|  |  |  | RACK |  |  |  | XARM |  |  | 1.4%: COPPER OPEN WIRE OHMS / 1000 FT
AMPACITY | SIZE |  | V - DROP |  | % DROP |  | V - DROP |  | % DROP |  | 1.4%: SIZE; 1.6%: R 75 C | X-RACK | X-XARM |  | Z-RACK |  | Z-XARM
| 6/1 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 6/1; 1.6%: 0.4925 | 0.1206 | 0.12988 |  | 0.49582 |  | 0.49986
| 6/3 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 6/3; 1.6%: 0.4993 | 0.1185 | 0.12778 |  | 0.50102 |  | 0.50507
| 4/1 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 4/1; 1.6%: 0.3103 | 0.1153 | 0.12458 |  | 0.32953 |  | 0.33357
| 4/3 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 4/3; 1.6%: 0.3136 | 0.1134 | 0.12268 |  | 0.33167 |  | 0.33571
| 2 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 2; 1.6%: 0.1992 | 0.1087 | 0.11798 |  | 0.22666 |  | 0.23071
| 1/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 1/0; 1.6%: 0.1254 | 0.1034 | 0.11268 |  | 0.15793 |  | 0.16198
| 2/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 2/0; 1.6%: 0.0994 | 0.1008 | 0.11008 |  | 0.1334 |  | 0.13744
| 3/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 3/0; 1.6%: 0.0791 | 0.0956 | 0.10488 |  | 0.11286 |  | 0.11691
| 4/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 4/0; 1.6%: 0.0629 | 0.0941 | 0.10338 |  | 0.097627 |  | 0.10167
| 500 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 500; 1.6%: 0.0271 | 0.0843 | 0.093578 |  | 0.061136 |  | 0.06518
[6 empty] | DROP | AMP CHK | FLICKER | Ampacity
|  |  | WIRE REF | 1 |  | 0 | OK | 0 | 100
|  | 1 | #6 CU | OK | 0 | 1 |  | 0 | 100
|  | 2 | #4 AL | OK | 0 | 1 |  | 0 | 100
|  | 3 | #4 CU | OK | 0 | 1 |  | 0 | 135
|  | 4 | #2 AL | OK | 0 | 1 |  | 0 | 135
|  | 5 | #2 CU | OK | 0 | 1 |  | 0 | 180
|  | 6 | 1/0 AL | OK | 0 | 1 |  | 0 | 180
|  | 7 | 3/0 AL | OK | 0 | 1 |  | 0 | 250
|  | 8 | 336.4 AL | OK | 0 | 1 |  | 0 | 400
|  | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE | LCR @ 240 |  | 1.3%: OLD 98 VALUES
|  | 1 | 1 |  |  | 1HP | 0.75 | 41.4096 | 27 |  | 1.3%: 48
|  | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096 | 34 |  | 1.3%: 60
|  | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096 | 46 |  | 1.3%: 72
|  | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096 | 69 |  | 1.3%: 102
|  | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096 | 103 |  | 1.3%: 135
|  | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096 | 115 |  | 1.3%: 168
|  | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096 | 140 |  | 1.3%: 197
|  | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096 | 175 |  | 1.3%: 240
|  | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096 | 218 |  | 1.3%: 300
|  | SINGLE PHASE LOOKUPS |  | Single PH Motor REF |  | 6 |  | LRC | 115
[6 empty] | 5 |  | P.F. | 0.75
[8 empty] | ANGLE | 41.4096
LRC VALUES (updated 5 FEB 1998)
SINGLE-PHASE MOTOR SIZES IN HP
|  | VOLTAGE | 1 | 1.5 | 2
|  | 120 | 46 | 69 | 92
LRC VALUES (updated 5 FEB 1998)
SINGLE-PHASE MOTOR SIZES IN HORSE POWER | bar: 1.2%
|  | VOLTAGE | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 1.2%: 10
|  | 240 | 27 | 34 | 46 | 69 | 103 | 115 | 140 | 175 | 1.2%: 218

## OHVDROPSEC1 (hidden)
Single PH Transformers |  |  | Lookup | 2 |  | Transformer Data |  |  |  |  | Correction Factor |  | 0 | 1
| Ref |  | Value |  | Tranfformer |  | R | X | X/R | Z% | 1.2% | 1.3% | 1.4% | 1.5% | 1.6% | 1.7%
| 1 |  | 10 |  | 10 KVA |  | 1.9% | 0.9% | 0.47368 | 2.102% | bar: 1.2% to 1.7%
| 2 |  | 15 |  | 15 KVA |  | 1.5% | 1.5% | 1 | 2.121% | bar: 1.2% to 1.7%
| 3 |  | 25 |  | 25 KVA |  | 1.4% | 1.4% | 1 | 1.98% | bar: 1.2% to 1.7%
| 4 |  | 37.5 |  | 37.5 KVA |  | 1.4% | 1.6% | 1.1429 | 2.126% | bar: 1.2% to 1.7%
| 5 |  | 50 |  | 50 KVA |  | 1.3% | 1.9% | 1.4615 | 2.302% | [9 empty] | Rt=Ro(1+aT) Ro=R0C | bar: 1.2% to 1.7%
| 6 |  | 75 |  | 75 KVA |  | 1.1% | 1.9% | 1.7273 | 2.195% | [9 empty] | COPPER a=0.004264 | [12 empty] | Transformer | Polemount Transformer Size - kVA | bar: 1.2% to 1.7%
| 7 |  | 100 |  | 100 KVA |  | 1.3% | 2% | 1.5385 | 2.385% | [9 empty] | ALUMINUM a=0.004200 | [12 empty] | Loading | 10 | 15 | 25 | 50 | 75 | 100 | bar: 1.2% to 1.7%
[11 empty] | 1.4%: %Vd =(Vd/Vab)*100 |  | %Vd = (KW/(Vo*cos a))*100*2Z/Vo | [14 empty] | 50% | 1.1 | 1 | 1.05 | 1.1 | 1.05 | 1
[11 empty] | 1.4%: Vd = IZ |  | T@nC=T@25C(234.5+T@nC)/259.5 | [14 empty] | 60% | 1.32 | 1.2 | 1.26 | 1.32 | 1.26 | 1.2
[11 empty] | 1.4%: KW = VIcos a => I = KW/(Vcos a) |  | X@D=X@1FOOT(0.528*LOGV@D-0.57) | [14 empty] | 70% | 1.54 | 1.4 | 1.47 | 1.54 | 1.47 | 1.4
[11 empty] | 1.4%: Z = Rcos a +Xsin a |  | D>1FOOT | [14 empty] | 80% | 1.76 | 1.6 | 1.68 | 1.76 | 1.68 | 1.6
| PF |  | < |  | 1-PH = 1 |  | SYSTEM |  | LOAD KW | [8 empty] | R1/R2=(234.5+T1)/(234.5+T2) | [14 empty] | 90% | 1.98 | 1.8 | 1.89 | 1.98 | 1.89 | 1.8
| 0.9 |  | 25.8419 |  | 3-PH = 3 |  | 1 |  | 0 | [7 empty] | Vd | [15 empty] | 100% | 2.2 | 2 | 2.1 | 2.2 | 2.1 | 2 | bar: 1.6% to 1.7%
[11 empty] | 1.6%: Vab; 1.7%: L | [16 empty] | 110% | 2.42 | 2.2 | 2.31 | 2.42 | 2.31 | 2.2
| VOLTAGE |  |  |  | RUNS |  | LENGTH FT |  | LINE-AMPS | [23 empty] | 120% | 2.64 | 2.4 | 2.52 | 2.64 | 2.52 | 2.4
| 120 |  | 240 |  | 1 |  | 0 |  | 0 | [23 empty] | 130% | 2.86 | 2.6 | 2.73 | 2.86 | 2.73 | 2.6
[33 empty] | 140% | 3.08 | 2.8 | 2.94 | 3.08 | 2.94 | 2.8
| kVA |  |  |  | 15 |  | 0 | Transformer Load kw | [24 empty] | 150% | 3.3 | 3 | 3.15 | 3.3 | 3.15 | 3
| Percentage Load |  |  |  | 0% |  | 4.5 | Motor Size | [24 empty] | 160% | 3.52 | 3.2 | 3.36 | 3.52 | 3.36 | 3.2
| %Transformer Volt Drop |  |  |  | 0% |  | 1.5% | Transformer %R | [17 empty] | POLYETHYLENE INSULATED ALUMINUM (WEATHERPROOF) | [6 empty] | 170% | 3.74 | 3.4 | 3.57 | 3.74 | 3.57 | 3.4
| %Transformer Flicker Drop |  |  |  | 3.489% |  | 1.5% | Transformer %X |  |  | 1.6%: CONDUCTOR DATA | [8 empty] | SIZE | 6 | 4 | 2 | 1/0 | 3/0 | 336.4
| POLYETHYLENE INSULATED ALUMINUM (WEATHERPROOF) | [9 empty] | 1.4%: POLYETHYLENE INSULATED ALUMINUM (WEATHERPROOF) OHMS/1000 FEET | [8 empty] | AMPACITY | 95 | 125 | 170 | 230 | 310 | 480
|  |  |  | RACK |  |  |  | XARM
AMPACITY | SIZE |  | V - DROP | FICKER | % DROP | % FLICKER | V - DROP |  | % DROP |  | 1.4%: SIZE; 1.6%: R 25 C | R 75 C | X-RACK |  | X-XARM |  | Z-RACK | Z-RACK F | Z-XARM
OK | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 6; 1.6%: 0.674 | 0.80387 | 0.128 |  | 0.13728 |  | 0.77927 | 0.68756 | 0.78332
OK | 4 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 4; 1.6%: 0.425 | 0.50689 | 0.125 |  | 0.13428 |  | 0.51069 | 0.46285 | 0.51473
OK | 2 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 2; 1.6%: 0.267 | 0.31845 | 0.126 |  | 0.13528 |  | 0.34152 | 0.32217 | 0.34557 |  | POLYETHYLENE INSULATED COPPER (WEATHERPROOF)
OK | 1/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 1/0; 1.6%: 0.168 | 0.20037 | 0.124 |  | 0.13328 |  | 0.23438 | 0.2323 | 0.23843 | SIZE | 6 | 4 | 2 | 1/0 | 2/0
OK | 3/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 3/0; 1.6%: 0.134 | 0.15982 | 0.122 |  | 0.13128 |  | 0.19702 | 0.20056 | 0.20106 | AMPACITY | 120 | 170 | 230 | 310
OK | 336.4 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 336.4; 1.6%: 0.106 | 0.12642 | 0.118 |  | 0.12728 |  | 0.16522 | 0.17287 | 0.16926
| POLYETHYLENE INSULATED COPPER (WEATHERPROOF) | [9 empty] | 1.4%: POLYETHYLENE INSULATED COPPER (WEATHERPROOF) OHMS/1000 FEET
|  |  |  | RACK |  |  |  | XARM
AMPACITY | SIZE |  | V - DROP |  | % DROP |  | V - DROP |  | % DROP |  | 1.4%: SIZE; 1.6%: R 25 C | R 75 C | X-RACK |  | X-XARM |  | Z-RACK |  | Z-XARM |  | RTS REVERSE TWIST SECONDARY ALUMINUM
OK | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 6; 1.6%: 0.419 | 0.49973 | 0.118 |  | 0.12728 |  | 0.50119 |  | 0.50524 | SIZE | 1/0 | 3/0 | 336.4
OK | 4 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 4; 1.6%: 0.2584 | 0.30819 | 0.118 |  | 0.12728 |  | 0.3288 |  | 0.33285 | AMPACITY | 180 | 250 | 400
OK | 2 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 2; 1.6%: 0.1626 | 0.19393 | 0.118 |  | 0.12728 |  | 0.22597 |  | 0.23002
OK | 1/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 1/0; 1.6%: 0.1022 | 0.12189 | 0.118 |  | 0.12728 |  | 0.16114 |  | 0.16518
OK | 2/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 2/0; 1.6%: 0.0811 | 0.096726 | 0.118 |  | 0.12728 |  | 0.13849 |  | 0.14253
[11 empty] | 1.4%: RTS REVERSE TWIST SECONDARY ALUMINUM | [9 empty] | SELF SUPPORTING SECONDARY TRIPLEX OR QUADRUPLEX
|  |  | RTS REVERSE TWIST SECONDARY ALUMINUM |  |  |  | Ser 3 |  | Ser 2 | [15 empty] | SIZE | 6 | 4 | 2 | 1/0 | 3/0
AMPACITY |  |  | SIZE | V - DROP | FICKER | % DROP | % Flicker |  | FICKER | % Flicker | 1.4%: SIZE; 1.6%: R 25 C | R 75 C | X |  | Z | Z FICKER 3 | Z FICKER 2 |  |  | AMPACITY (Tripx) | ------ | 100 | 135 | 180 | ------
OK |  |  | 2 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1.4%: 1/0; 1.6%: 0.1661 | 0.1981 | 0.039205 |  | 0.19538 | 0.14513 | 0.14513 |  |  | AMPACITY (Quadx) | ------ | ------ | 112 | ------ | 192
OK |  |  | 1/0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1.4%: 3/0; 1.6%: 0.1046 | 0.12475 | 0.036742 |  | 0.12829 | 0.11787 | 0.11787
OK |  |  | 3/0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1.4%: 336.4; 1.6%: 0.053 | 0.063212 | 0.0348 |  | 0.07206 | 0.070427 | 0.070427
OK |  |  | 336.4 | 0 | 0 | 0 | 0 |  | 0 | 0
THW COPPER WIRE
[11 empty] | 1.4%: SELF SUPPORTING SECONDARY WITH BARE NEUTRAL MESSENGER | [8 empty] | SIZE | 6 | 4 | 2 | 1/0 | 2/0 | 3/0 | 4/0 | 500
| SELF SUPPORTING SECONDARY TRIPLEX OR QUADRUPLEX | [23 empty] | AMPACITY | 96 | 125 | 170 | 230 | 265 | 310 | 360
Ser3 |  |  | ALUMINUM |  |  |  | COPPER |  |  | % FLICKER | 1.4%: ALUMINUM |  |  |  | COPPER
AMPACITY | SIZE |  | V - DROP | FICKER | % DROP | % FLICKER | V - DROP | FICKER | % DROP | Ser 3 | 1.2%: Ser 2; 1.6%: R 75 C | X | Z | Z Flicker | R 75 C |  | Z | Z FLICKER 3 | Z FLICKER2
OK | 6 |  | ---- | ---- | ---- | ---- | 0 | 0 | 0 | 0 | 1.2%: 0; 1.4%: 6 | 0.0489 |  |  | 0.4932 |  | 0.4652 | 0.40224 | 0.40224
OK | 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2%: 0; 1.4%: 4; 1.6%: 0.505 | 0.0466 | 0.47481 | 0.40957 | 0.3092 |  | 0.29859 | 0.26272 | 0.26272
OK | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2%: 0; 1.4%: 2; 1.6%: 0.321 | 0.0434 | 0.30782 | 0.26946 | 0.1957 |  | 0.19505 | 0.17548 | 0.17548 |  | OPEN COPPER WIRE BARE
OK | 1/0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 1.4%: 1/0; 1.6%: 0.2016 | 0.0392 | 0.19853 | 0.17713 | [5 empty] | SIZE | 6/1 | 6/3 | 4/1 | 4/3 | 2 | 1/0 | 2/0 | 3/0 | 4/0 | 500
OK | 3/0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 1.4%: 3/0; 1.6%: 0.126 | 0.0367 | 0.1294 | 0.11877 | [5 empty] | AMPACITY
Ser 2
| 6 |  | ---- | ---- | ---- | ---- | 0 | 0 | 0 |  | 1.7%: THW COPPER WIRE AND TREE WIRE
| 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6%: R 75 C | X-RACK | X-XARM |  | Z-RACK |  | Z-XARM
| 1/0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 1.4%: 6; 1.6%: 0.4932 | 0.0867 | 0.095978 |  | 0.48167 |  | 0.48572
| 3/0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 1.4%: 4; 1.6%: 0.3092 | 0.0813 | 0.090578 |  | 0.31372 |  | 0.31776
[11 empty] | 1.4%: 2; 1.6%: 0.1957 | 0.0754 | 0.084678 |  | 0.209 |  | 0.21304
[11 empty] | 1.4%: 1/0; 1.6%: 0.1282 | 0.0684 | 0.077678 |  | 0.14519 |  | 0.14924
[11 empty] | 1.4%: 2/0; 1.6%: 0.0981 | 0.0652 | 0.074478 |  | 0.11671 |  | 0.12075
[11 empty] | 1.4%: 3/0; 1.6%: 0.0787 | 0.0625 | 0.071778 |  | 0.098073 |  | 0.10212
[11 empty] | 1.4%: 4/0; 1.6%: 0.0622 | 0.0589 | 0.068178 |  | 0.081654 |  | 0.085698
[11 empty] | 1.4%: 500; 1.6%: 0.0276 | 0.0458 | 0.055078 |  | 0.044804 |  | 0.048848
OPEN COPPER WIRE BARE
|  |  |  | RACK |  |  |  | XARM |  | % FLICKER | 1.4%: COPPER OPEN WIRE OHMS / 1000 FT
AMPACITY | SIZE |  | V - DROP |  | % DROP | FICKER | V - DROP | FICKER | % DROP | Ser 3 | 1.2%: Ser 2; 1.4%: SIZE; 1.6%: R 75 C | X-RACK | X-XARM |  | Z-RACK 3 | Z-RACK 2 | Z-XARM 3 | Z-XARM 2 | [8 empty] | 5
| 6/1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2%: 0; 1.4%: 6/1; 1.6%: 0.4925 | 0.1206 | 0.12988 |  | 0.44914 | 0.44914 | 0.45528 | 0.45528
| 6/3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2%: 0; 1.4%: 6/3; 1.6%: 0.4993 | 0.1185 | 0.12778 |  | 0.45286 | 0.45286 | 0.45899 | 0.45899
| 4/1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2%: 0; 1.4%: 4/1; 1.6%: 0.3103 | 0.1153 | 0.12458 |  | 0.30899 | 0.30899 | 0.31513 | 0.31513
| 4/3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2%: 0; 1.4%: 4/3; 1.6%: 0.3136 | 0.1134 | 0.12268 |  | 0.31021 | 0.31021 | 0.31634 | 0.31634
| 2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2%: 0; 1.4%: 2; 1.6%: 0.1992 | 0.1087 | 0.11798 |  | 0.2213 | 0.2213 | 0.22744 | 0.22744
| 1/0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2%: 0; 1.4%: 1/0; 1.6%: 0.1254 | 0.1034 | 0.11268 |  | 0.16244 | 0.16244 | 0.16858 | 0.16858
| 2/0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2%: 0; 1.4%: 2/0; 1.6%: 0.0994 | 0.1008 | 0.11008 |  | 0.14122 | 0.14122 | 0.14736 | 0.14736
| 3/0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2%: 0; 1.4%: 3/0; 1.6%: 0.0791 | 0.0956 | 0.10488 |  | 0.12256 | 0.12256 | 0.1287 | 0.1287
| 4/0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2%: 0; 1.4%: 4/0; 1.6%: 0.0629 | 0.0941 | 0.10338 |  | 0.10942 | 0.10942 | 0.11555 | 0.11555
| 500 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2%: 0; 1.4%: 500; 1.6%: 0.0271 | 0.0843 | 0.093578 |  | 0.076084 | 0.076084 | 0.082221 | 0.082221
% FLICKER | bar: 1.2%
|  |  |  | WIRE REF |  | DROP | AMP CHK | FLICKER | Ampacity | Ser 3 | 1.2%: Ser 2
|  |  | Wire | 6 |  | 0 | OK | 0 | 180 | 0 | 1.2%: 0
|  | 1 | #6 CU | OK | 0 | 1 | 0 | 0 | 100
|  | 2 | #4 AL | OK | 0 | 1 | 0 | 0 | 100
|  | 3 | #4 CU | OK | 0 | 1 | 0 | 0 | 135 |  | 1.2%: Ser3
|  | 4 | #2 AL | OK | 0 | 1 | 0 | 0 | 135 |  | 1.2%: Ser2
|  | 5 | #2 CU | OK | 0 | 1 | 0 | 0 | 180
|  | 6 | 1/0 AL | OK | 0 | 1 | 0 | 0 | 180
|  | 7 | 3/0 AL | OK | 0 | 1 | 0 | 0 | 250
|  | 8 | 336.4 AL | OK | 0 | 1 | 0 | 0 | 400
|  | 9 | #6 WP CU | OK | 0 | 1 | 0 | 0 | 120
|  | 10 | #4 WP CU | OK | 0 | 1 | 0 | 0 | 170
|  | 11 | #2 WP CU | OK | 0 | 1 | 0 | 0 | 230
|  | 12 | 1/0 WP CU | OK | 0 | 1 | 0 | 0 | 310 |  | 1.3%: OLD 98 VALUES
|  | 1 | 1 |  |  | 1HP | 0.75 | 41.4096 | 27 |  | 1.3%: 48
|  | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096 | 34 |  | 1.3%: 60
|  | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096 | 46 |  | 1.3%: 72
|  | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096 | 69 |  | 1.3%: 102
|  | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096 | 103 |  | 1.3%: 135
|  | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096 | 115 |  | 1.3%: 168
|  | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096 | 140 |  | 1.3%: 197
|  | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096 | 175 |  | 1.3%: 240
|  | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096 | 218 |  | 1.3%: 300
|  | SINGLE PHASE LOOKUPS |  | Single PH Motor REF |  | 5 |  | LRC | 103
[6 empty] | 4.5 |  | P.F. | 0.75
|  | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE | 41.4096
LRC VALUES (updated 5 FEB 1998)
SINGLE-PHASE MOTOR SIZES IN HP
|  | VOLTAGE | 1 | 1.5 | 2
|  | 120 | 46 | 69 | 92
LRC VALUES (updated 5 FEB 1998)
SINGLE-PHASE MOTOR SIZES IN HORSE POWER | bar: 1.2%
|  | VOLTAGE | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 1.2%: 10
|  | 240 | 27 | 34 | 46 | 69 | 103 | 115 | 140 | 175 | 1.2%: 218

## OHVDROPSEC2 (hidden)
Single PH Transformers |  |  | Lookup | 2 |  | Transformer Data |  |  |  |  | Correction Factor |  | 0 | 1
| Ref |  | Value |  | Tranfformer |  | R | X | X/R | Z% | 1.2% | 1.3% | 1.4% | 1.5% | 1.6% | 1.7%
| 1 |  | 10 |  | 10 KVA |  | 1.9% | 0.9% | 0.47368 | 2.102% | bar: 1.2% to 1.7%
| 2 |  | 15 |  | 15 KVA |  | 1.5% | 1.5% | 1 | 2.121% | bar: 1.2% to 1.7%
| 3 |  | 25 |  | 25 KVA |  | 1.4% | 1.4% | 1 | 1.98% | bar: 1.2% to 1.7%
| 4 |  | 37.5 |  | 37.5 KVA |  | 1.4% | 1.6% | 1.1429 | 2.126% | bar: 1.2% to 1.7%
| 5 |  | 50 |  | 50 KVA |  | 1.3% | 1.9% | 1.4615 | 2.302% | [9 empty] | Rt=Ro(1+aT) Ro=R0C | bar: 1.2% to 1.7%
| 6 |  | 75 |  | 75 KVA |  | 1.1% | 1.9% | 1.7273 | 2.195% | [9 empty] | COPPER a=0.004264 | [12 empty] | Transformer | Polemount Transformer Size - kVA | bar: 1.2% to 1.7%
| 7 |  | 100 |  | 100 KVA |  | 1.3% | 2% | 1.5385 | 2.385% | [9 empty] | ALUMINUM a=0.004200 | [12 empty] | Loading | 10 | 15 | 25 | 50 | 75 | 100 | bar: 1.2% to 1.7%
[11 empty] | 1.4%: %Vd =(Vd/Vab)*100 |  | %Vd = (KW/(Vo*cos a))*100*2Z/Vo | [14 empty] | 50% | 1.1 | 1 | 1.05 | 1.1 | 1.05 | 1
[11 empty] | 1.4%: Vd = IZ |  | T@nC=T@25C(234.5+T@nC)/259.5 | [14 empty] | 60% | 1.32 | 1.2 | 1.26 | 1.32 | 1.26 | 1.2
[11 empty] | 1.4%: KW = VIcos a => I = KW/(Vcos a) |  | X@D=X@1FOOT(0.528*LOGV@D-0.57) | [14 empty] | 70% | 1.54 | 1.4 | 1.47 | 1.54 | 1.47 | 1.4
[11 empty] | 1.4%: Z = Rcos a +Xsin a |  | D>1FOOT | [14 empty] | 80% | 1.76 | 1.6 | 1.68 | 1.76 | 1.68 | 1.6
| PF |  | < |  | 1-PH = 1 |  | SYSTEM |  | LOAD KW | [8 empty] | R1/R2=(234.5+T1)/(234.5+T2) | [14 empty] | 90% | 1.98 | 1.8 | 1.89 | 1.98 | 1.89 | 1.8
| 0.9 |  | 25.8419 |  | 3-PH = 3 |  | 1 |  | 0 | [7 empty] | Vd | [15 empty] | 100% | 2.2 | 2 | 2.1 | 2.2 | 2.1 | 2 | bar: 1.6% to 1.7%
[11 empty] | 1.6%: Vab; 1.7%: L | [16 empty] | 110% | 2.42 | 2.2 | 2.31 | 2.42 | 2.31 | 2.2
| VOLTAGE |  |  |  | RUNS |  | LENGTH FT |  | LINE-AMPS | [23 empty] | 120% | 2.64 | 2.4 | 2.52 | 2.64 | 2.52 | 2.4
| 120 |  | 240 |  | 1 |  | 0 |  | 0 | [23 empty] | 130% | 2.86 | 2.6 | 2.73 | 2.86 | 2.73 | 2.6
[33 empty] | 140% | 3.08 | 2.8 | 2.94 | 3.08 | 2.94 | 2.8
| kVA |  |  |  | 15 |  | 0 | Transformer Load kw | [24 empty] | 150% | 3.3 | 3 | 3.15 | 3.3 | 3.15 | 3
| Percentage Load |  |  |  | 0% |  | 1 | Motor Size |  | Transformer Flicker by service | [22 empty] | 160% | 3.52 | 3.2 | 3.36 | 3.52 | 3.36 | 3.2
| %Transformer Volt Drop |  |  |  | 0% | 0.9146% | 1.5% | Transformer %R |  | Ser1 | 1.2%: 0.9146% | [9 empty] | POLYETHYLENE INSULATED ALUMINUM (WEATHERPROOF) | [6 empty] | 170% | 3.74 | 3.4 | 3.57 | 3.74 | 3.57 | 3.4
| %Transformer Flicker Drop |  |  |  | 0.9146% | 0.9146% | 1.5% | Transformer %X |  | Ser2 | 1.2%: 0.9146%; 1.6%: CONDUCTOR DATA | [8 empty] | SIZE | 6 | 4 | 2 | 1/0 | 3/0 | 336.4
| POLYETHYLENE INSULATED ALUMINUM (WEATHERPROOF) | [8 empty] | Ser 3 | 1.2%: 0.9146%; 1.4%: POLYETHYLENE INSULATED ALUMINUM (WEATHERPROOF) OHMS/1000 FEET | [8 empty] | AMPACITY | 95 | 125 | 170 | 230 | 310 | 480
|  |  |  | RACK |  |  |  | XARM
AMPACITY | SIZE |  | V - DROP | FICKER | % DROP | % FLICKER | V - DROP |  | % DROP |  | 1.4%: SIZE; 1.6%: R 25 C | R 75 C | X-RACK |  | X-XARM |  | Z-RACK | Z-RACK F | Z-XARM
OK | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 6; 1.6%: 0.674 | 0.80387 | 0.128 |  | 0.13728 |  | 0.77927 | 0.68756 | 0.78332
OK | 4 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 4; 1.6%: 0.425 | 0.50689 | 0.125 |  | 0.13428 |  | 0.51069 | 0.46285 | 0.51473
OK | 2 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 2; 1.6%: 0.267 | 0.31845 | 0.126 |  | 0.13528 |  | 0.34152 | 0.32217 | 0.34557 |  | POLYETHYLENE INSULATED COPPER (WEATHERPROOF)
OK | 1/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 1/0; 1.6%: 0.168 | 0.20037 | 0.124 |  | 0.13328 |  | 0.23438 | 0.2323 | 0.23843 | SIZE | 6 | 4 | 2 | 1/0 | 2/0
OK | 3/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 3/0; 1.6%: 0.134 | 0.15982 | 0.122 |  | 0.13128 |  | 0.19702 | 0.20056 | 0.20106 | AMPACITY | 120 | 170 | 230 | 310
OK | 336.4 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 336.4; 1.6%: 0.106 | 0.12642 | 0.118 |  | 0.12728 |  | 0.16522 | 0.17287 | 0.16926
| POLYETHYLENE INSULATED COPPER (WEATHERPROOF) | [9 empty] | 1.4%: POLYETHYLENE INSULATED COPPER (WEATHERPROOF) OHMS/1000 FEET
|  |  |  | RACK |  |  |  | XARM
AMPACITY | SIZE |  | V - DROP |  | % DROP |  | V - DROP |  | % DROP |  | 1.4%: SIZE; 1.6%: R 25 C | R 75 C | X-RACK |  | X-XARM |  | Z-RACK |  | Z-XARM |  | RTS REVERSE TWIST SECONDARY ALUMINUM
OK | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 6; 1.6%: 0.419 | 0.49973 | 0.118 |  | 0.12728 |  | 0.50119 |  | 0.50524 | SIZE | 1/0 | 3/0 | 336.4
OK | 4 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 4; 1.6%: 0.2584 | 0.30819 | 0.118 |  | 0.12728 |  | 0.3288 |  | 0.33285 | AMPACITY | 180 | 250 | 400
OK | 2 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 2; 1.6%: 0.1626 | 0.19393 | 0.118 |  | 0.12728 |  | 0.22597 |  | 0.23002
OK | 1/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 1/0; 1.6%: 0.1022 | 0.12189 | 0.118 |  | 0.12728 |  | 0.16114 |  | 0.16518
OK | 2/0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 1.4%: 2/0; 1.6%: 0.0811 | 0.096726 | 0.118 |  | 0.12728 |  | 0.13849 |  | 0.14253
[11 empty] | 1.4%: RTS REVERSE TWIST SECONDARY ALUMINUM | [9 empty] | SELF SUPPORTING SECONDARY TRIPLEX OR QUADRUPLEX
|  |  | RTS REVERSE TWIST SECONDARY ALUMINUM | [21 empty] | SIZE | 6 | 4 | 2 | 1/0 | 3/0
AMPACITY |  |  | SIZE | V - DROP | FICKER | % DROP | % FLICKER |  |  |  | 1.4%: SIZE; 1.6%: R 25 C | R 75 C | X |  | Z | Z FICKER |  |  |  | AMPACITY (Tripx) | ------ | 100 | 135 | 180 | ------
OK |  |  | 2 | 0 | 0 | 0 | 0 |  |  |  | 1.4%: 1/0; 1.6%: 0.1661 | 0.1981 | 0.039205 |  | 0.19538 | 0.17451 |  |  |  | AMPACITY (Quadx) | ------ | ------ | 112 | ------ | 192
OK |  |  | 1/0 | 0 | 0 | 0 | 0 | 180 |  |  | 1.4%: 3/0; 1.6%: 0.1046 | 0.12475 | 0.036742 |  | 0.12829 | 0.11787
OK |  |  | 3/0 | 0 | 0 | 0 | 0 | 250 |  |  | 1.4%: 336.4; 1.6%: 0.053 | 0.063212 | 0.0348 |  | 0.07206 | 0.070427
OK |  |  | 336.4 | 0 | 0 | 0 | 0 | 400
THW COPPER WIRE
[11 empty] | 1.4%: SELF SUPPORTING SECONDARY WITH BARE NEUTRAL MESSENGER | [8 empty] | SIZE | 6 | 4 | 2 | 1/0 | 2/0 | 3/0 | 4/0 | 500
| SELF SUPPORTING SECONDARY TRIPLEX OR QUADRUPLEX | [23 empty] | AMPACITY | 96 | 125 | 170 | 230 | 265 | 310 | 360
|  |  | ALUMINUM |  |  |  | COPPER |  |  |  | 1.4%: ALUMINUM |  |  |  | COPPER
AMPACITY | SIZE |  | V - DROP | FICKER | % DROP | % FLICKER | V - DROP | FICKER | % DROP | % FLICKER | 1.6%: R 75 C | X | Z | Z Flicker | R 75 C |  | Z | Z FLICKER
OK | 6 |  | ---- | ---- | ---- | ---- | 0 | 0 | 0 | 0 | 1.4%: 6 | 0.0489 |  |  | 0.4932 |  | 0.4652 | 0.40224
OK | 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4%: 4; 1.6%: 0.505 | 0.0466 | 0.47481 | 0.40957 | 0.3092 |  | 0.29859 | 0.26272
OK | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4%: 2; 1.6%: 0.321 | 0.0434 | 0.30782 | 0.26946 | 0.1957 |  | 0.19505 | 0.17548 |  |  | OPEN COPPER WIRE BARE
OK | 1/0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 1.4%: 1/0; 1.6%: 0.2016 | 0.0392 | 0.19853 | 0.17713 | [5 empty] | SIZE | 6/1 | 6/3 | 4/1 | 4/3 | 2 | 1/0 | 2/0 | 3/0 | 4/0 | 500
OK | 3/0 |  | 0 | 0 | 0 | 0 |  |  |  |  | 1.4%: 3/0; 1.6%: 0.126 | 0.0367 | 0.1294 | 0.11877 | [5 empty] | AMPACITY
|  |  |  | THW COPPER WIRE | [6 empty] | 1.7%: THW COPPER WIRE AND TREE WIRE
|  |  |  | RACK |  |  |  | XARM
AMPACITY | SIZE |  | V - DROP |  | % DROP |  | V - DROP |  | % DROP |  | 1.6%: R 75 C | X-RACK | X-XARM |  | Z-RACK |  | Z-XARM
| 6 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 6; 1.6%: 0.4932 | 0.0867 | 0.095978 |  | 0.48167 |  | 0.48572
| 4 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 4; 1.6%: 0.3092 | 0.0813 | 0.090578 |  | 0.31372 |  | 0.31776
| 2 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 2; 1.6%: 0.1957 | 0.0754 | 0.084678 |  | 0.209 |  | 0.21304
| 1/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 1/0; 1.6%: 0.1282 | 0.0684 | 0.077678 |  | 0.14519 |  | 0.14924
| 2/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 2/0; 1.6%: 0.0981 | 0.0652 | 0.074478 |  | 0.11671 |  | 0.12075
| 3/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 3/0; 1.6%: 0.0787 | 0.0625 | 0.071778 |  | 0.098073 |  | 0.10212
| 4/0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 4/0; 1.6%: 0.0622 | 0.0589 | 0.068178 |  | 0.081654 |  | 0.085698
| 500 |  | 0 |  | 0 |  | 0 |  | 0 |  | 1.4%: 500; 1.6%: 0.0276 | 0.0458 | 0.055078 |  | 0.044804 |  | 0.048848
OPEN COPPER WIRE BARE
|  |  |  | RACK |  |  |  | XARM |  |  | 1.4%: COPPER OPEN WIRE OHMS / 1000 FT
AMPACITY | SIZE |  | V - DROP |  | % DROP |  | V - DROP | FICKER | % DROP | % FLICKER | 1.4%: SIZE; 1.6%: R 75 C | X-RACK | X-XARM |  | Z-RACK |  | Z-XARM
| 6/1 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 1.4%: 6/1; 1.6%: 0.4925 | 0.1206 | 0.12988 |  | 0.49582 |  | 0.49986
| 6/3 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 1.4%: 6/3; 1.6%: 0.4993 | 0.1185 | 0.12778 |  | 0.50102 |  | 0.50507
| 4/1 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 1.4%: 4/1; 1.6%: 0.3103 | 0.1153 | 0.12458 |  | 0.32953 |  | 0.33357
| 4/3 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 1.4%: 4/3; 1.6%: 0.3136 | 0.1134 | 0.12268 |  | 0.33167 |  | 0.33571
| 2 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 1.4%: 2; 1.6%: 0.1992 | 0.1087 | 0.11798 |  | 0.22666 |  | 0.23071
| 1/0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 1.4%: 1/0; 1.6%: 0.1254 | 0.1034 | 0.11268 |  | 0.15793 |  | 0.16198
| 2/0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 1.4%: 2/0; 1.6%: 0.0994 | 0.1008 | 0.11008 |  | 0.1334 |  | 0.13744
| 3/0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 1.4%: 3/0; 1.6%: 0.0791 | 0.0956 | 0.10488 |  | 0.11286 |  | 0.11691
| 4/0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 1.4%: 4/0; 1.6%: 0.0629 | 0.0941 | 0.10338 |  | 0.097627 |  | 0.10167
| 500 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 1.4%: 500; 1.6%: 0.0271 | 0.0843 | 0.093578 |  | 0.061136 |  | 0.06518
[6 empty] | DROP | AMP CHK | FLICKER | Ampacity
|  |  | WIRE REF | 6 |  | 0 | OK | 0 | 180
|  | 1 | #6 CU | OK | 0 | 1 |  | 0 | 100
|  | 2 | #4 AL | OK | 0 | 1 |  | 0 | 100
|  | 3 | #4 CU | OK | 0 | 1 |  | 0 | 135
|  | 4 | #2 AL | OK | 0 | 1 |  | 0 | 135
|  | 5 | #2 CU | OK | 0 | 1 |  | 0 | 180
|  | 6 | 1/0 AL | OK | 0 | 1 |  | 0 | 180
|  | 7 | 3/0 AL | OK | 0 | 1 |  | 0 | 250
|  | 8 | 336.4 AL | OK | 0 | 1 |  | 0 | 400
|  | 9 | #6 WP CU | OK | 0 | 1 |  | 0 | 120
|  | 10 | #4 WP CU | OK | 0 | 1 |  | 0 | 170
|  | 11 | #2 WP CU | OK | 0 | 1 |  | 0 | 230
|  | 12 | 1/0 WP CU | OK | 0 | 1 |  | 0 | 310 |  | 1.3%: OLD 98 VALUES
|  | 1 | 1 |  |  | 1HP | 0.75 | 41.4096 | 27 |  | 1.3%: 48
|  | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096 | 34 |  | 1.3%: 60
|  | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096 | 46 |  | 1.3%: 72
|  | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096 | 69 |  | 1.3%: 102
|  | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096 | 103 |  | 1.3%: 135
|  | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096 | 115 |  | 1.3%: 168
|  | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096 | 140 |  | 1.3%: 197
|  | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096 | 175 |  | 1.3%: 240
|  | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096 | 218 |  | 1.3%: 300
|  | SINGLE PHASE LOOKUPS |  | Single PH Motor REF |  | 1 |  | LRC | 27
[6 empty] | 1 |  | P.F. | 0.75
|  | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE | 41.4096
LRC VALUES (updated 5 FEB 1998)
SINGLE-PHASE MOTOR SIZES IN HP
|  | VOLTAGE | 1 | 1.5 | 2
|  | 120 | 46 | 69 | 92
LRC VALUES (updated 5 FEB 1998)
SINGLE-PHASE MOTOR SIZES IN HORSE POWER | bar: 1.2%
|  | VOLTAGE | 1 | 1.5 | 2 | 3 | 4.5 | 5 | 6 | 7.5 | 1.2%: 10
|  | 240 | 27 | 34 | 46 | 69 | 103 | 115 | 140 | 175 | 1.2%: 218

## Trans Data (hidden)
Single Phase Transformer Data |  |  | Padmount |  |  | Single Phase Transformer Data |  |  | Polemount
| R | X | Z |  |  | 10 KVA |  | 1.9% | 0.9% | 0.47368 | 2.102%
15 | 1.7 | 1.2 | 2.1 |  |  | 15 KVA |  | 1.5% | 1.5% | 1 | 2.121%
25 | 1.6 | 1.2 | 2 |  |  | 25 KVA |  | 1.4% | 1.4% | 1 | 1.98%
50 | 1.3 | 1.7 | 2.1 |  |  | 37.5 KVA |  | 1.4% | 1.6% | 1.1429 | 2.126%
75 | 1.1 | 1.8 | 2 |  |  | 50 KVA |  | 1.3% | 1.9% | 1.4615 | 2.302%
100 | 1.1 | 1.9 | 2.2 |  |  | 75 KVA |  | 1.1% | 1.9% | 1.7273 | 2.195%
167 | 1.1 | 2 | 2.3 |  |  | 100 KVA |  | 1.3% | 2% | 1.5385 | 2.385%
3 Phase | Transformer Data 208 |  |  |  | Table 4 - Three-Phase Padmount Transformer- 480 V
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  | LOOK UP FOR MOTORS |  |  |  |  | PF | ANGLE
Trans |  |  | X/R |  |  |  | X/R |  |  | 1 | 1 |  |  | 1HP | 0.75 | 41.4096
(kVA) | R | X | Ratio | Z% | R | X | Ratio | Z% |  | 2 | 1.5 | 1 | 1 TON | 1.5HP 1 TON | 0.75 | 41.4096
45 | 1.91% | 1.93% | 1.0105 | 2.715% | [5 empty] | 3 | 2 | 1.5 | 1.5 TON | 2 HP 1.5TON | 0.75 | 41.4096
75 | 1.72% | 1.51% | 0.87791 | 2.289% | 1.62% | 1.46% | 0.90123 | 2.181% |  | 4 | 3 | 2 | 2 TON | 3 HP 2 TON | 0.75 | 41.4096
150 | 1.14% | 1.54% | 1.3509 | 1.916% | 1.25% | 1.47% | 1.176 | 1.93% |  | 5 | 4.5 | 3 | 3 TON | 4.5HP 3 TON | 0.75 | 41.4096
225 | 1.19% | 1.54% | 1.2941 | 1.946% | 0.88% | 1.32% | 1.5 | 1.586% |  | 6 | 5 | 3.5 | 3.5 TON | 5 HP 3.5TON | 0.75 | 41.4096
300 | 1.02% | 2.05% | 2.0098 | 2.29% | 1.16% | 1.77% | 1.5259 | 2.116% |  | 7 | 6 | 4 | 4 TON | 6 HP 4 TON | 0.75 | 41.4096
500 | 0.81% | 4.43% | 5.4691 | 4.503% | 0.9% | 2.07% | 2.3 | 2.257% |  | 8 | 7.5 | 5 | 5 TON | 7.5HP 5 TON | 0.75 | 41.4096
750 | 0.95% | 5.97% | 6.2842 | 6.045% | 0.82% | 5.81% | 7.0854 | 5.868% |  | 9 | 10 | 7 | 7 TON | 10 HP 7 TON | 0.75 | 41.4096
1000 | 0.9% | 5.75% | 6.3889 | 5.82% | 0.86% | 5.83% | 6.7791 | 5.893%
1500 |  |  |  |  | 0.72% | 6.02% | 8.3611 | 6.063%
2000 |  |  |  |  | 0.67% | 5.86% | 8.7463 | 5.898%
2500 |  |  |  |  | 0.77% | 5.77% | 7.4935 | 5.821%
3000 |  |  |  |  | 0.77% | 5.79% | 7.5195 | 5.841%