Work Paper WPSDGENRHC1010

Revision 0

San Diego Gas & Electric

Energy Efficiency Engineering

Commercial Evaporator Coil Cleaning

# Work Paper Approvals

| Charles Harmstead | 6/4/2012 Date |
| --- | --- |
|  | Date |
|  | Date |

# At a Glance Summary

| Applicable Measure Codes: | WPSDNRHC – EvapCoilClean |
| --- | --- |
| Measure Description: | Commercial Evaporator Coil Cleaning |
| Energy Impact Common Units: | Tons Served |
| Base Case Description: | Commercial Evaporator Coil Cleaning |
| Base Case Energy Consumption: | 2,705 kWh |
| Measure Energy Consumption: | 2,629 kWh |
| Energy Savings (Base Case – Measure) | 77 kWh |
| Costs Common Units: | Tons served |
| Base Case Equipment Cost ($/unit): | $0 |
| Measure Equipment Cost ($/unit): | $35.11 |
| Measure Incremental Cost ($/unit): | $35.11 |
| Effective Useful Life (years): | 3 years |
| Program Type: | RET (Retrofit) |
| Net-to-Gross Ratios: | .73 |
| Important Comments: | SDG&E 2006-08 Workpaper Msr#263006 |

# Document Revision History

| Revision No. | Date | Author | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 6/4/2112 | Charles Harmstead | Adopted from Conservation Services Group WPSDNRHC-EvapCoilClean Rev0. Updated NTG to DEER 2011 |

- Table of Contents

Work Paper Approvals	ii

At a Glance Summary	iii

Document Revision History	iv

Section 1. General Measure & Baseline Data	1

1.1Measure & Delivery Description	1

1.2 DEER Differences Analysis	1

1.3 Code Analysis	1

1.4 Measure Effective Useful Life	1

1.5 Net-to-Gross Ratios for Different Program Strategies	1

1.6 Gross Realization Rate	1

1.7 Time-of-Use Adjustment Factor	2

Section 2. Energy Savings & Demand Reduction Calculations	3-7

Section 3. Load Shapes	7

Section 4. Base Case & Measure Costs	7-8

4.1 Base Case Cost	7-8

4.2 Gross Measure Cost	8

4.3 Incremental Measure Cost (For DEEMED measures only)	8

Attachments	9

References	10

# Section 1. General Measure & Baseline Data

## Measure & Delivery Description

Evaporator Coil Cleaning improves heat transfer and efficiency in commercial HVAC units.  Over time, the evaporator coil may accumulate dust and debris which interfere with heat transfer properties and degrade the performance of the AC unit.  This measure is performed by  licensed HVAC contractors as part of a comprehensive AC tune-up service.  Participating Commercial HVAC contractors market the tune-ups to their customers, enabling the program to target hard-to-reach market segments.  Website, direct outreach, and program marketing materials distributed through business and trade associations enable greater penetration into targeted market segments.  This service is provided to customers at low or no cost, depending on prices set by participating contractors.

## 1.2 DEER Differences Analysis

DEER does not have an evaporator coil cleaning measure, but baseline data for annual kWh and kW usage for commercial HVAC units is available on DEER.  Baseline data for Commercial Condenser Coil Cleaning was used for this measure to provide baseline and measure data points, but the energy savings came directly from existing SDG&E Workpapers from the 2006-08 program cycle.  The kWh savings, however, appeared high, despite positive EM&V findings. For this paper, the kWh values were adjusted downward by 50% to reflect best estimates of typical deemed savings for the measure, but the kW savings were adopted as is.

## 1.3 Code Analysis

California’s Title 24 Building Energy Efficiency Standards include provisions for increasing the efficiency of HVAC  replacement units beginning January 1, 2010. The code effects on this measure are minimal and indirect.  Because higher efficiency units are typically more expensive than the prior standard, some customers may be inclined to continue to use their existing units rather than upgrade to the new efficiency standard.  This may serve to increase demand for HVAC tune-ups and the need for the evaporator coil cleaning measure.

1.4 Measure Effective Useful Life

Value: 3 years, based on SDG&E 2006-08 Workpaper Msr#263006.

## 1.5 Net-to-Gross Ratios for Different Program Strategies

The NTGR default value (0.73) for “HVAC Maintenance Refrigerant Charge Adjustment” from DEER 2011_NTGR_2012-05-16.xls was adopted this measure.  Evaporator coil cleaning is performed as HVAC maintenance generally while refrigerant charge adjustments are also performed.

## 1.6 Gross Realization Rate

1.0 based on Direct Installation.

## 1.7 Time-of-Use Adjustment Factor

100% (NR-HVAC)

# Section 2. Energy Savings & Demand Reduction Calculations

Deemed Savings based on SDG&E Workpaper Measure #263006 and DEER 2008 Commercial Results Review-NonUpdated Measures.xls for condenser coil cleaning primary End-Use kWh.

Assumptions:

Conversion factor based on 2006-07 SDG&E Workpaper Measure #263006

kWh savings were adjusted by 50% and divided by 5 tons per average unit to bring savings in line with comparable measures on the program where DEER data is available.

kW savings were divided by average 5 tons per unit but were not adjusted due to comparability with similar program measures.

Measure 263006 savings:	766.82	Gross kWh/AC Unit

(per AC unit)			0.11		Gross kW/AC Unit

`

No vintage or climate distinction

Measure Life: 3 years

50% adjustment (kWh)	0.5

Conversion to tons			0.2		1 unit = 5 tons (for purposes of converting DEER

baseline data to units from the workpaper.  This did not affect the savings estimate, which came directly from the workpaper prior to scale adjustment as noted.

Adjusted savings		76.682	Gross kWh/ton

0.022	Gross kW/ton

# Section 3. Load Shapes

01-ALC-AllCommercial-Cooling

# Section 4. Base Case & Measure Costs

## 4.1 Base Case Cost

Base case cost is zero.  It is a retrofit measure.

## 4.2 Gross Measure Cost

Retrofit DEEMED Direct Install

Gross Measure Cost is not available in DEER measure costs, however, a similar measure, Clean Condenser Coils is included in DEER 2005 and DEER 2008.  The 2006-08 SDG&E Workpaper for measure #263006 estimates the cost of this measure at $86.30 per AC unit.  The 2008 Revised DEER Measure Cost Summary puts the cost of the Clean Condenser Coils measure at $158.34 per ton.  The 2005 DEER cost for the measure was $35.11.  Evaporator Coil Cleaning is a comparable measure to Condenser Coil Cleaning in the amount of labor required and the cost of materials, therefore the value for Condenser Coil Cleaning appears an appropriate proxy for this measure.  However, because the DEER 2008 revised value appears too high, and the SDG&E Workpaper measure (which applies primarily to smaller HVAC units) appears low, the 2005 DEER Measure value was taken.  This provides some consistency in incentive levels and TRC calculations from the 2006-09 program to the 2010-12 cycle.

Source: DEER 2005 Measure Costs, 2006-08 SDG&E Workpaper Measure #263006, Revised DEER Measure Cost Summary (05_30_2008) Revised (06_02_2008).xls posted on DEER website.  Downloaded 9/30/2009.

## 4.3 Incremental Measure Cost (For DEEMED measures only)

Retrofit DEEMED Direct Install  - $35.11 per ton

Source: DEER 2005.  See discussion above.

# Attachments

WPSDNRHCEvapCoilClean

2006_08_Q3 Program Workpapers

EUL Summary

Updated DEER NTGR Values

Revised DEER Cost Summary

# References

“NTG Values – To be used for 16 February 2009 Supplemental 2009-11 Application Filings (same as previous 2009-2011 planning values)”  2008 Database for Energy-Efficient Resources Version 2008.2.05 December 16, 2008.  For use in the California IOU 2009-2011 Energy Efficiency Planning and Reporting.  Updated DEER NTGR Values – 053008.xls

May 30, 2008. Retrieved January 18,2010 from www.deeresources.com/

“Technology and Measure Cost Data”  2008 Database for Energy-Efficient Resources Version 2008.2.05 December 16, 2008.  For use in the California IOU 2009-2011 Energy Efficiency Planning and Reporting.  Revised DEER Measure Cost Summary (05_30_2008).xls.

May 30, 2008. Retrieved January 18,2010 from www.deeresources.com/

San Diego Gas & Electric 2006-08 Program Cycle Workpapers, page 155.  Measure #263006.  3P Mobile Energy Clinic (MEC).  Dated 11/21/2007.

EM&V Study of the ADM Mobile Energy Clinic 2004-05 Non-Utility Energy Efficiency Program Implementations Program 1105-04 – SDG&E Service Territory, Program 1106-04 – SCE Service Territory, Program 1487-04 SCG Service Territory.  August 16, 2006  Final Report.  Sisson and Associates, Inc. (S&A), San Rafael, CA.  Retrieved January 17, 2010 from www.calmac.org