Work Paper WPSDGENRHC1030

Revision 0

San Diego Gas & Electric

Energy Efficiency Engineering

Air Filter Replacement

# At a Glance Summary

| Measure Name: | Air Filter Replacement |
| --- | --- |
| Savings Impacts Common Units: | Tons Served |
| Customer Base Case Description: | Dirty/Restrictive Air Filter |
| Code Base Case Description: | N/A |
| Costs Common Units: | Tons Served |
| Measure Equipment Cost ($/unit): | $2.15 |
| Measure Incremental Cost ($/unit): | $8.00 |
| Measure Installed Cost ($/unit): | $10.15 |
| Measure Load Shape: | Non Residential Cooling (load-shapes plotted below) |
| Effective Useful Life (years): | 1 year |
| Program Type: | Retrofit |
| TOU AC Adjustment: | 100% |
| Net-to-Gross Ratios: | 0.73 |
| Important Comments: |  |

| Work Paper RunID | Building Type | Building Vintage | CZ | Customer Annual Electric Savings (kWh/unit) | Customer Peak Electric Demand Reduction (kW/unit) | Customer Annual Natural Gas Savings (Therms/unit) | Above Code Annual Electric Savings (kWh/unit) | Above Code Peak Electric Demand Reduction (kW/unit) | Above Code Annual Natural Gas Savings (Therms/unit) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Office – Small | Before 1978 | 7 | 60.89 | 0.013 | 0 | 60.89 | 0.013 | 0 |
| 2 | Office – Small | 1978-1992 | 7 | 50.10 | 0.012 | 0 | 50.10 | 0.012 | 0 |
| 3 | Office – Small | Before 1978 | 10 | 77.33 | 0.018 | 0 | 77.33 | 0.018 | 0 |
| 4 | Office – Small | 1978-1992 | 10 | 64.17 | 0.016 | 0 | 64.17 | 0.016 | 0 |
| 5 | Retail – Small | Before 1978 | 7 | 57.68 | 0.020 | 0 | 57.68 | 0.020 | 0 |
| 6 | Retail – Small | 1978-1992 | 7 | 46.21 | 0.017 | 0 | 46.21 | 0.017 | 0 |
| 7 | Retail – Small | Before 1978 | 10 | 75.75 | 0.021 | 0 | 75.75 | 0.021 | 0 |
| 8 | Retail – Small | 1978-1992 | 10 | 61.49 | 0.018 | 0 | 61.49 | 0.018 | 0 |
| 9 | Retail – Single Story Large | Before 1978 | 7 | 52.19 | 0.020 | 0 | 52.19 | 0.020 | 0 |
| 10 | Retail – Single Story Large | 1978-1992 | 7 | 42.36 | 0.017 | 0 | 42.36 | 0.017 | 0 |
| 11 | Retail – Single Story Large | Before 1978 | 10 | 64.19 | 0.021 | 0 | 64.19 | 0.021 | 0 |
| 12 | Retail – Single Story Large | 1978-1992 | 10 | 52.06 | 0.018 | 0 | 52.06 | 0.018 | 0 |
| 13 | Restaurant – Sit Down | Before 1978 | 7 | 55.82 | 0.013 | 0 | 55.82 | 0.013 | 0 |
| 14 | Restaurant – Sit Down | 1978-1992 | 7 | 45.01 | 0.012 | 0 | 45.01 | 0.012 | 0 |
| 15 | Restaurant – Sit Down | Before 1978 | 10 | 90.13 | 0.018 | 0 | 90.13 | 0.018 | 0 |
| 16 | Restaurant – Sit Down | 1978-1992 | 10 | 73.59 | 0.016 | 0 | 73.59 | 0.016 | 0 |

# Document Revision History

| # Revision | # Date | # Description | # Author (Company) |
| --- | --- | --- | --- |
| # Revision 0 | # 6/6/2012 | # Developed from Matrix Energy Services, Inc workpaper WPMSDGEAF0408, Revision1. Revised NTGR for 2012 DEER | # Charles Harmstead (SDGE) |

# Table of Contents

At a Glance Summary	i

Document Revision History	iii

Table of Contents	iv

List of Tables	v

List of Figures	v

Section 1. General Measure & Baseline Data	6

1.1 Measure Description & Background	6

1.2 DEER Differences Analysis	6

1.3 Codes & Standards Requirements Analysis	6

1.4 EM&V, Market Potential, and Other Studies	6

1.5 Base Cases for Savings Estimates: Existing & Above Code	6

Energy Savings	6

Demand Reduction	7

1.6 Base Cases & Measure Effective Useful Lives	7

1.7 Net-to-Gross Ratios for Different Program Strategies	7

Section 2. Calculation Methods	8

2.1 Energy Savings Estimation Methodologies	8

2.2. Demand Reduction Estimation Methodologies	8

Section 3. Load Shapes	9

3.1 Base Cases Load Shapes	9

3.2 Measure Load Shapes	10

Section 4. Base Case & Measure Costs	10

4.1 Base Cases Costs	10

4.2 Measure Costs	10

4.3 Incremental & Full Measure Costs	10

References	11

# List of Tables

Table 1: DEER runs used to establish baseline energy usages.	6

Table 2: Net-to-Gross Ratios from DEER	7

Table 3: Base case energy usages per ton for targeted building types and climate zones.	8

Table 4: Estimated energy savings per ton for targeted building types and climate zones.	8

Table 5: Base case peak demands for targeted building types and climate zones.	8

Table 6: Estimated demand reduction for targeted building types and climate zones.	9

# List of Figures

Figure 1: Base case electric load shapes for summer weekdays.	9

Figure 2: Measure load shapes for summer weekdays.	10

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

Replace dirty disposable air filters in rooftop packaged air conditioning units.  Air filters become more restrictive as they accumulate particulate matter.  Scheduled replacement of air filters saves energy by reducing the workload for the air-handling unit and by protecting the evaporator coils, thus preserving optimal heat transfer.  Dirty air filters result in longer AC run times.

## 1.2 DEER Differences Analysis

This measure does not exist in the DEER database.  However, eQUEST 3.54/DEER 2.1 models1 were used to establish the baseline energy usages to which the measure savings apply.

## 1.3 Codes & Standards Requirements Analysis

There are no relevant codes/standards pertaining to this measure.

## 1.4 EM&V, Market Potential, and Other Studies

This measure has been evaluated by Sisson and Associates2 for general retail establishments.

## 1.5 Base Cases for Savings Estimates: Existing & Above Code

## Energy Savings

The DEER was used in conjunction with our experience implementing similar ‘Mobile Energy Clinic’ (MEC) programs to establish the baseline energy usages.  DEER runs are used to obtain energy demand and usage per area for the targeted building types and climate zones. Our field experience and recorded data from the Mobile Energy Clinic program provides us with program-specific estimates of the average building sizes and tonnage of air conditioning for the targeted building types, and we opt to use these values than the somewhat less specific DEER values.   The following DEER runs are used for developing base case energy usages:

Table 1

DEER runs used to establish baseline energy usages.

| DEER Runs | DEER Runs | DEER Runs | DEER Runs |
| --- | --- | --- | --- |
| COfS1075APA11 | CRtL0775APA11 | CRSD0775APA11 | CRtS1075APA11 |
| COfS1085APA11 | CRtL0785APA11 | CRSD0785APA11 | CRtS1085APA11 |
| COfS0775APA11 | CRtL1075APA11 | CRSD1075APA11 | CRtS0775APA11 |
| COfS0785APA11 | CRtL1085APA11 | CRSD1085APA11 | CRtS0785APA11 |

From these runs we obtained three values:

- Primary End Use (kWh/ton)

- Number of Tons

- Area (square footage)

These values were used to obtain kWh per square foot in the following manner:

(kWh/ton) * (tons) / (square footage) = (kWh/sqft)

The following is an example of this calculation done for DEER Run IDCOfS1075APA11:

(1478.20 kWh/ton) * (35.872 tons) / (10,002.30 sqft) = 5.3014 kWh/sqft

Next, we used actual findings in the field to convert this value back into kWh per ton.  In our experience implementing Mobile Energy Clinic, we have found the following average values:

Average area (sqft) of business participant = 1495 sqft

Average number of HVAC units per business participant = 1.36 units

Average tons per HVAC unit serviced under program = 3.35 tons

The following equation was used in the conversion:

(kWh/sqft) * (Ave square footage/site) / (Ave tons) / (Ave No. units/site) = (Average kWh/ton)

Continuing the example from above:

(5.3014 kWh/sqft) *(1495 sqft/site) / (3.35 tons) / (1.36 units/site) = 1739.59 kWh/ton

This process was used to estimate baseline energy usages to which the relative energy savings apply.

## Demand Reduction

DEER eQuest was used to establish the baseline peak coincident demands to which the measure savings apply.  The program was run using DEER input models used to populate the DEER itself.  The debug output was used to obtain the peak coincident “Space Cooling” demand.  The tons were calculated by dividing the kWh savings by kWh savings per ton.

## 1.6 Base Cases & Measure Effective Useful Lives

The EUL for air filters is 1 year; taken from Sisson2, page 72.

## 1.7 Net-to-Gross Ratios for Different Program Strategies

NTGR provided from DEER 2011 NonRes-sAll-mHVAC-RCA, HVAC Maintenance: Refrigerant Charge Adjustment (RCA).This measure is performed generally when RCA is performed

Table 2

Net-to-Gross Ratios from DEER

| Program Type | NTGR |
| --- | --- |
| All Other Nonresidential Programs | 0.73 |

# Section 2. Calculation Methods

## 2.1 Energy Savings Estimation Methodologies

A savings of 3.5% relative to the base case is obtained from the Sisson and Associates EM&V report2, page 65.  The base case energy usages, obtained from the aforementioned DEER eQUEST runs and MEC data as described in Section 1.5, are listed for the targeted climate zones and building types in Table 3 below.

Table 3

Base case energy usages per ton for targeted building types and climate zones.

| Baseline Energy Usage (kWh/ton) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone | Small Office Pre 1978 | Small Office 1979-1992 | Small Retail Pre 1978 | Small Retail 1979-1992 |
| CZ-07 | 1739.59 | 1431.53 | 1647.98 | 1320.22 |
| CZ-10 | 2209.54 | 1833.37 | 2164.27 | 1756.98 |
| Climate Zone | Large Retail Pre 1978 | Large Retail 1979-1992 | Restaurant Pre 1978 | Restaurant 1979-1992 |
| CZ-07 | 1491.00 | 1210.18 | 1594.91 | 1286.02 |
| CZ-10 | 1833.94 | 1487.41 | 2575.17 | 2102.46 |

Energy savings are estimated by applying the 3.5% energy savings factor to the base case energy usages.  The savings are listed in Table 4 below.

Table 4

Estimated energy savings per ton for targeted building types and climate zones.

| Energy Savings (kWh/ton) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone | Small Office Pre 1978 | Small Office 1979-1992 | Small Retail Pre 1978 | Small Retail 1979-1992 |
| CZ-07 | 60.89 | 50.10 | 57.68 | 46.21 |
| CZ-10 | 77.33 | 64.17 | 75.75 | 61.49 |
| Climate Zone | Large Retail Pre 1978 | Large Retail 1979-1992 | Restaurant Pre 1978 | Restaurant 1979-1992 |
| CZ-07 | 52.19 | 42.36 | 55.82 | 45.01 |
| CZ-10 | 64.19 | 52.06 | 90.13 | 73.59 |

## 2.2. Demand Reduction Estimation Methodologies

The savings of 1.75% relative to the base case can be applied directly to the base case peak coincident demand (e.g. largest hourly average kW for 2PM to 5PM on summer weekdays) for space cooling.  The base case demands, obtained from the aforementioned DEER eQUEST runs, are listed for each targeted building type and climate zone in Table 5 below.

Table 5

Base case peak demands for targeted building types and climate zones.

| Peak Coincident Demand for Pre-1993 Vintage (kW/ton) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone | Small Office Pre 1978 | Small Office 1979-1992 | Small Retail Pre 1978 | Small Retail 1979-1992 |
| CZ-07 | 0.758 | 0.659 | 1.167 | 0.977 |
| CZ-10 | 1.016 | 0.890 | 1.215 | 1.026 |

Demand reductions are estimated by applying the 1.75% relative savings to the base case peak coincident demands.   The demand savings are listed for each targeted building type and climate zone in Table 6 below.

Table 6

Estimated demand reduction for targeted building types and climate zones.

| Peak Coincident Demand Reduction (kW/ton) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Climate Zone | Small Office Pre 1978 | Small Office 1979-1992 | Small Retail Pre 1978 | Small Retail 1979-1992 |
| CZ-07 | 0.013 | 0.012 | 0.020 | 0.017 |
| CZ-10 | 0.018 | 0.016 | 0.021 | 0.018 |

The per-ton demand reductions for large retail and sit-down restaurants were taken to be the same as small retail and small office respectfully.

# Section 3. Load Shapes

## 3.1 Base Cases Load Shapes

The load shapes for the targeted building types in SDG&E service territory are obtained from CEUS data4.   The load shapes are then scaled such that the peak electric demand for the day matches the entry for the corresponding building type and climate zone as shown in Table 5 above.   The base-case load shapes are shown for three building types in Figure 1.  A spreadsheet that constructs the load shapes using peak demands from the DEER/MEC data and the load shapes from CEUS is attached at the end of this report5.

Figure 1: Base case electric load shapes for summer weekdays.

## 3.2 Measure Load Shapes

The measure load shapes are the products of the relative savings (1.75%) times the base load shapes.  The measure load shapes are an hourly profile of the kW savings per unit expected from the measure, and are provided in Figure 2 below.

Figure 2: Measure load shapes for summer weekdays.

# Section 4. Base Case & Measure Costs

## 4.1 Base Cases Costs

- None.

## 4.2 Measure Costs

- $2.15 per ton for materials.

- $8.00 per ton for labor.

These costs are market costs obtained from conversations with various HVAC contractors, and from previous experience with various ‘Mobile Energy Clinic’ programs2 conducted for SDG&E, SCE, and SCG.

## 4.3 Incremental & Full Measure Costs

- This is a direct install program.

- The installed costs are $2.15 + $8.00 = $10.15 per ton.

# References

- The eQuest 3.56 Deer 2.1 version of eQuest can be used to recreate the weather sensitive savings reported in the official 2.1 version of the DEER database. 
 http://doe2.com/download/DEER/MAStool/eQUEST-DEERv3-54_Setup.exe

- “EM&V STUDY OF THE ADM MOBILE ENERGY CLINIC 2004-2005 NON-UTILITY ENERGY EFFICIENCY PROGRAM IMPLEMENTATIONS” Program 1105-04 – SDG&E Service Territory, Final Report dated August 16, 2006 and Worksheets, submitted by Sisson and Associates, Inc.

- DEER 2011 NTGR table:

- Data from the CEUS survey are available online at http://capabilities.itron.com/CeusWeb/Chart.aspx.
We downloaded the ’16 Day Type’ Excel spreadsheets for the appropriate building types in SDG&E territory, and used the AC end-use load shape for the ‘hot summer weekday’.  See tab named ‘CEUS Example –exp16Day’ in the spreadsheet provided in reference 5 below.

- The results of the DEER runs, as well as the load shapes from CEUS data, and the resulting base-case and measure load shapes, are included in the following spreadsheet: