Work Paper WPSDGENRHC1050 Revision 0

San Diego Gas & Electric

Energy Efficiency Engineering

Guest Room PTAC/PTHP Energy Management System

# Work Paper Approvals

| Charles Harmstead Supervisor, Energy Efficiency Engineering | Date |
| --- | --- |
| Peter Ford Manager, Energy Efficiency Engineering | Date |

# At a Glance Summary

| Applicable Measure Codes: | WPSDNRHC_PTACPTHPEMS See attached spreadsheet for measure codes. | WPSDNRHC_PTACPTHPEMS See attached spreadsheet for measure codes. |
| --- | --- | --- |
| Measure Description: | Telkonet SmartEnergy is an occupancy-sensor based Energy Management System installed in conjunction with packaged terminal air-conditioners or packaged terminal heat pumps in hotel or motel guest rooms. | Amana is an occupancy-sensor based Energy Management System installed in conjunction with packaged terminal air-conditioners or packaged terminal heat pumps in hotel or motel guest rooms. |
| Energy Impact Common Units: | tons served | tons served |
| Base Case Description: | 6.50 EER to 10.5 EER (based on vintage) package terminal A/C; 6.50 EER / 2.7 COP to 10.5 EER (based on vintage) package terminal HP | 6.50 EER to 10.5 EER (based on vintage) package terminal A/C; 6.50 EER / 2.7 COP to 10.5 EER (based on vintage) package terminal HP |
| Base Case Energy Consumption: | 2172.95 kWh – Climate Zone 6, 7 or 8 1999.10 kWh – Climate Zone 10, 14 or 15 | 1240 kWh – Climate Zone 6, 7 or 8 1649 kWh – Climate Zone 10, 14 or 15 |
| Measure Energy Consumption: | 1691.95 kWh – Climate Zone 6, 7 or 8 1535.60 kWh – Climate Zone 10, 14 or 15 | 894 kWh – Climate Zone 6, 7 or 8 1122 kWh – Climate Zone 10, 14 or 15 |
| Energy Savings (Base Case – Measure) | 481.0 kWh – Climate Zone 6, 7 or 8 463.5 kWh – Climate Zone 10, 14 or 15 | 346 kWh – Climate Zone 6, 7 or 8 527 kWh – Climate Zone 10, 14 or 15 |
| Costs Common Units: | Per ton. | Per ton. |
| Base Case Equipment Cost ($/ton): | $0 | $0 |
| Measure Equipment Cost ($/ton): | $346.19 | $365.00 |
| Measure Incremental Cost ($/ton): | $346.19 | $365.00 |
| Effective Useful Life (years): | 11 years | 11 years |
| Program Type: | RETROFIT | RETROFIT |
| Net-to-Gross Ratios: | .85 | .85 |
| Important Comments: |  |  |

# Document Revision History

| Revision No. | Date | Author | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 01/19/2010 | Liz DeSouza/CSG | Original work paper (short form) |
| 1 | 04/20/2010 | Liz DeSouza/CSG | Reduced savings percentage, based on Emerging Technology Study; adjusted units to per-ton. |
| 0 | 08/17/2012 | Kelvin Valenzuela/ SDG&E | Adopted from Work Paper WPSDNRHC_PTACEMS rev1.doc, updated 4/20/12. Updated NTG values to DEER 2011. Added savings for Amana EMS controls. Savings are referenced from Emerging Technology study. (August 29,2012) |

- Table of Contents

Work Paper Approvals	ii

At a Glance Summary	ii

Document Revision History	iii

Section 1. General Measure & Baseline Data	2

1.1Measure & Delivery Description	2

1.2 DEER Differences Analysis	2

1.3 Code Analysis	2

1.4 Measure Effective Useful Life	2

1.5 Net-to-Gross Ratios for Different Program Strategies	2

1.6 Gross Realization Rate	2

1.7 Time-of-Use Adjustment Factor	2

Section 2. Energy Savings & Demand Reduction Calculations	2

Section 3. Load Shapes	2

Section 4. Base Case & Measure Costs	3

4.1 Base Case Cost	3

4.2 Gross Measure Cost	3

4.3 Incremental Measure Cost (For DEEMED measures only)	3

Attachments	4

References	5

# Section 1. General Measure & Baseline Data

## Measure & Delivery Description

Telkonet/Smart Systems International (SSI) EMS system is installed in guest rooms with existing PTAC or PTHP units.  Each installation includes a power controller and an occupancy sensor, which are governed by a patented recovery-time process which guarantees system performance.  When the room is unoccupied, the power controller allows the temperature in the room to drift to a set-point to reduce PTAC/PTHP runtime.  The prescribed set-point governs maximum recovery time upon room occupation from the unoccupied temperature.

Amana has a product similar to the Telkonet product.  Main difference is that the Amana thermostat units set back the temperature incrementally depending on the length of time that the room is unoccupied.  This is different than the Telkonet unit were it set backs the temperature  based on heat gain and solar exposure, such that each room is set back to a different temperature so that recovery to the customer’s preferred setting is a fixed amount of time.  And because the Telkonet units do not vary the setback with time since last occupied, the Telkonet units may setback when unoccupied for period less than three hours.

Delivery will be a combination of Direct Install, On Bill Financing, and Customer Prescriptive Rebates aimed at hard-to-reach market segments.  Installation will be limited to hotels or motels built before 2010.

## 1.2 DEER Differences Analysis

DEER D03-073 (Run ID CHTl077PrTSt) provides savings and cost data for “installing programmable thermostats in older buildings,” accounting for EImpacts of  454.522 kWh/1000 square feet, therm savings based on a gas/electric HVAC system, and negative kW savings.  DEER D03-072 (Run ID CHtl0775HCEMS) provides data for “Suite of EMS measures” with respect to installations at hotels where a central plant system is used. This measure differs from the first two measures in that the savings unit is per ton of cooling, the building type is limited to Hotel and Motel Guest Rooms, and the heating/cooling system is packaged terminal air conditioning or heat pumps (PTAC/PTHP).  Because very few hotel rooms are 1000 square feet, the tonnage of the unit is a more direct measure of the energy usage.  PTAC and PTHP units are all-electric, with no gas component for heating.  The EMS Controller in this work paper includes occupancy sensors for each room, such that controllers are more responsive to occupancy than a typical set-back thermostat.  Run-time reductions are expected year-round, with the potential for summer peak demand reductions.  Cost data is taken directly from DEER D08-NE-HVAC-Timeclocks.

## 1.3 Code Analysis

California’s Title 24 Building Energy Efficiency Standards include provisions for increasing the efficiency of PTAC/PTHP replacement units beginning January 1, 2010 to 10.9 EER and new construction units to 12.5 EER.  The code effects on EMS Controller savings is insignificant because direct installations and customer incentives will be targeted specifically at existing building stock and existing PTAC/PTHP units.  The indirect effects of the increased efficiency requirement for PTAC and PTHP units is that costs of replacement are higher, leading more customers to use existing equipment longer rather than replace it.  This may assist the market for PTAC/PTHP controllers as customers seek to reduce their energy costs with the lowest initial cost investment.

1.4 Measure Effective Useful Life

Value: 11 years, based on DEER value for Setback Programmable Thermostats or Time Clocks (heating/cooling).  New or Replacement on Burnout.  SERRA Report 2005 uses 14 years for Install HVAC EMS – Com 14 (policy manual tab in E3 Calculator) but the more conservative value is used here.

## 1.5 Net-to-Gross Ratios for Different Program Strategies

DEER 2011 recommend a net-to-gross ratio (NTGR) of 0.85 for all energy efficiency measures (EEMs) covered under this program5.  The referenced NTGR table suggest the 0.85 value for NTGR for the category labeled “All other EEMs with no evaluated NTGR; direct install to hard-to-reach only”.  Guest room PTAC/PTHP Energy Management System fall into this category.

## 1.6 Gross Realization Rate

1.0 based on Direct Installation.

## 1.7 Time-of-Use Adjustment Factor

100% (NR-HVAC)

# Section 2. Energy Savings & Demand Reduction Calculations

Deemed Savings based on DEER 2008 Commercial Results Review-NonUpdated Measures.xls for PTHP2 and PTAC2 equipment, Primary End-Use kWh/unit and manufacturer data.

Energy savings (kWh/tons served) = .2214 runtime reduction x Customer Base (coastal)

.2318 runtime reduction x Customer Base (inland)

(Deemed Customer Base from DEER 2008 Commercial Results Review-NonUpdated Measures.xls)

Demand Reduction based on PCimpact/ECImpact x Energy Savings (from above).

Assumptions:

Manufacturer calculations place ex-ante reduction in run-hours at 45%, however, ex-post savings provided by manufacturer average 28%.  See attached files provided by Telkonet.  New information from “Hotel Guest Room Energy Controls” San Diego Gas & Electric Emerging Technologies Program. December 2008 found increased heating usage with similar occupancy sensors.  Baseline usage from DEER NonUpdated measures file was preserved, but savings are reduced to 22.14% (coastal zones) and 23.18% (inland zones) to reflect average climate zone findings per ton of cooling from the above report.  Savings values were taken directly from this report, irrespective of measured baselines, and percentages were adjusted accordingly using DEER baseline data.

See workpaper for savings per climate zone and vintage.

Climate Zone 7 savings are representative of all coastal zones in the area (6, 7 or 8), and Climate Zone 10 savings are representative of all inland zones (10, 14, 15) due to high proportion of hotels/motels in these two zones.  This measure will be targeted toward all eligible hotels and motels in any of the above climate zones.  Savings will be reported based on DEER baseline data multiplied by the run-time reductions noted above.

# Section 3. Load Shapes

11-HTL-Lodging–Hotel(GuestRooms)-COOL

# Section 4. Base Case & Measure Costs

## 4.1 Base Case Cost

Source: Revised DEER Measure Cost Summary (05_30_2008) Revised (06_02_2008).xls posted on DEER website.  Downloaded 9/30/2009.  NR – Misc & HVAC,  Time clocks (heating/cooling) D08-NE-HVAC-Timeclocks.  Material Cost: $162.08, 2.50 Installation Man Hours – Retrofit, $184.11 Installation Labor Cost-Retrofit.

## 4.2 Gross Measure Cost

Retrofit DEEMED Direct Install

Source: Revised DEER Measure Cost Summary (05_30_2008) Revised (06_02_2008).xls posted on DEER website.  Downloaded 9/30/2009.  NR – Misc & HVAC,  Time clocks (heating/cooling) D08-NE-HVAC-Timeclocks.  Material Cost: $162.08, 2.50 Installation Man Hours – Retrofit, $184.11 Installation Labor Cost-Retrofit.

## 4.3 Incremental Measure Cost (For DEEMED measures only)

Retrofit DEEMED Direct Install

Source: Revised DEER Measure Cost Summary (05_30_2008) Revised (06_02_2008).xls posted on DEER website.  Downloaded 9/30/2009.  NR – Misc & HVAC,  Time clocks (heating/cooling) D08-NE-HVAC-Timeclocks.  Material Cost: $162.08, 2.50 Installation Man Hours – Retrofit, $184.11 Installation Labor Cost-Retrofit.

# Attachments

# References

- Savings Calculations for Intown - St Charles, MO (2008) provided by Telkonet via e-mail.

- Measurement and Verification Processes and Guidelines (2008) provided by Telkonet via e-mail.

- Assumptions and Savings Calculations for San Diego Climate Zones provided by Telkonet via e-mail.

- Description of measure features as provided for Ecology Action – LodgingSavers. (2009, August 21). PG&E 2009-2011 Energy Efficiency Program workpapers.

- DEER 2011 Net-To-Gross Ratios.  (“DEER2011-NTG_IncludingCarryoversFromDEER2008_2011-12-07.xls”, accessed March 26, 2012 at http://www.deeresources.com/index).

- “Technology and Measure Cost Data”  2008 Database for Energy-Efficient Resources Version 2008.2.05 December 16, 2008.  For use in the California IOU 2009-2011 Energy Efficiency Planning and Reporting.  Revised DEER Measure Cost Summary (05_30_2008).xls.  May 30, 2008. Retrieved January 18,2010 from www.deeresources.com/

7.	“Hotel Guest Room Energy Controls” San Diego Gas and Electric Emerging Technologies Program.  December 2008.  Project Manager AY Ahmed, San Diego Gas & Electric.  Prepared by Theresa Pistochini, California Lighting Technology Center, Kristin Heinemeier, Western Cooling Efficiency Center, and Daryl DeJean, Emerging Technologies Associates, Inc.