Work Paper WPSDGENRHC1051

- Revision 0

San Diego Gas & Electric

Energy Efficiency Engineering

Guest Room PTAC/PTHP Adaptive Climate Controller

# Work Paper Approvals

| Charles Harmstead Supervisor, Energy Efficiency Engineering; Date. Peter Ford Manager, Energy Efficiency Engineering; Date. |  |
| --- | --- |

# At a Glance Summary

| Applicable Measure Codes: | WPSDAllVintAllCZGuestRmPTACPTHPACC See attached spreadsheet for list of applicable measure codes. |
| --- | --- |
| Measure Description: | Guest Rm PTAC/PTHP Adaptive Climate Controller |
| Energy Impact Common Units: | Tons cooling |
| Base Case Description: | PTAC/PTHP 6.8 EER to 10.16 EER |
| Base Case Energy Consumption: | 2,306.017 kWh |
| Measure Energy Consumption: | 1,660.332 kWh |
| Energy Savings (Base Case – Measure) | 645.685 kWh |
| Costs Common Units: | Number of Installations |
| Base Case Equipment Cost ($/unit): | $346.19 |
| Measure Equipment Cost ($/unit): | $346.19 |
| Measure Incremental Cost ($/unit): | $346.19 |
| Effective Useful Life (years): | 11 years |
| Program Type: | RET (Retrofit) |
| Net-to-Gross Ratios: | 0.85 |
| Important Comments: |  |

# Document Revision History

| Revision No. | Date | Author | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 1/19/2010 | Liz DeSouza/CSG | Original work paper (short form) |
| 0 | 8/17/2012 | Kelvin Valenzuela/SDGE | Adopted from WorkPaper WPSDNRHC_PTACACCfinal.doc, updated January 19, 2010. Updated NTG values to DEER 2011 (Updated August 30, 2012) |

- Table of Contents

Work Paper Approvals	ii

At a Glance Summary	ii

Document Revision History	iii

Section 1. General Measure & Baseline Data	1

1.1Measure & Delivery Description	1

1.2 DEER Differences Analysis	1

1.3 Code Analysis	1

1.4 Measure Effective Useful Life	2

1.5 Net-to-Gross Ratios for Different Program Strategies	2

1.6 Gross Realization Rate	2

1.7 Time-of-Use Adjustment Factor	2

Section 2. Energy Savings & Demand Reduction Calculations	2

Section 3. Load Shapes	3

Section 4. Base Case & Measure Costs	3

4.1 Base Case Cost	3

4.2 Gross Measure Cost	3

4.3 Incremental Measure Cost (For DEEMED measures only)	3

Attachments	4

References	5

# Section 1. General Measure & Baseline Data

## Measure & Delivery Description

The Adaptive Climate Controller (ACC) is a sensor-based controller installed in hotel or motel guest rooms with existing PTAC or PTHP units.  Each installation includes an Optically Programmable (OP) controller combination which continually monitors, controls, powers and regulates the speed of fractional horsepower AC motors.  This technology is applicable to most single phase AC induction motors up to 240 VAC and 10 amps, and can be used to upgrade unit ventilators, fan coils, PTACs and exhaust fans.  Developed in conjunction with the Department of Energy’s EERE Industrial Technologies Program, this technology can reduce electrical energy use by over 30%.  Delivery will be a combination of Direct Install, On Bill Financing, and Customer Prescriptive Rebates aimed at hard-to-reach market segments.  Installation will be limited to hotels or motels built before 2010 (not new construction).

## 1.2 DEER Differences Analysis

DEER D03-073 (Run ID CHTl077PrTSt) provides savings and cost data for “installing programmable thermostats in older buildings,” accounting for EImpacts of 454.522 kWh/1000 square feet, therm savings based on a gas/electric HVAC system, and negative kW savings.  DEER D03-072 (Run ID CHtl0775HCEMS) provides data for “Suite of EMS measures” with respect to installations at hotels where a central plant system is used. This measure differs from the first two measures in that the savings unit is per ton of cooling, the building type is limited to Hotel and Motel Guest Rooms, and the heating/cooling system is packaged terminal air conditioning or heat pumps (PTAC/PTHP).  PTAC and PTHP units are all-electric, with no gas component for heating.  The Controller in this work paper continually monitors power and motor speed in order to achieve savings when the unit is running.  Run-time reductions are expected year-round, with the potential for summer peak demand reductions.  Cost data is taken directly from DEER D08-NE-HVAC-Timeclocks.

## 1.3 Code Analysis

California’s Title 24 Building Energy Efficiency Standards include provisions for increasing the efficiency of PTAC/PTHP replacement units beginning January 1, 2010 to 10.9 EER and new construction units to 12.5 EER.  The code effects on EMS Controller savings is insignificant because direct installations and customer incentives will be targeted specifically at existing building stock and existing or replacement PTAC/PTHP units installed prior to 2010.  The indirect effects of the increased efficiency requirement for PTAC and PTHP units is that costs of replacement are higher, leading more customers to use existing equipment longer rather than replace it.  This may assist the market for PTAC/PTHP controllers as customers seek to reduce their energy costs with the lowest initial cost investment.

1.4 Measure Effective Useful Life

Value: 11 years, based on DEER value for Setback Programmable Thermostats or Time Clocks (heating/cooling).  New or Replacement on Burnout.  See EUL_Summary_10-1-08.xls attached. SERRA Report 2005 uses 14 years for Install HVAC EMS – Com 14 (policy manual tab in E3 Calculator) but the more conservative value is used here.

## 1.5 Net-to-Gross Ratios for Different Program Strategies

DEER 2011 recommend a net-to-gross ratio (NTGR) of 0.85 for all energy efficiency measures (EEMs) covered under this program1.  The referenced NTGR table suggest the 0.85 value for NTGR for the category labeled “All other EEMs with no evaluated NTGR; direct install to hard-to-reach only”.  Guest room PTAC/PTHP Energy Management System fall into this category.

## 1.6 Gross Realization Rate

1.0 based on Direct Installation.

## 1.7 Time-of-Use Adjustment Factor

100% (NR-HVAC)

# Section 2. Energy Savings & Demand Reduction Calculations

Deemed Savings based on DEER 2008 Commercial Results Review-NonUpdated Measures.xls for PTHP2 and PTAC2 equipment, Primary End-Use kWh/unit and manufacturer data.

Energy savings (kWh/tons served) = .30 efficiency improvement x Customer Base

(Deemed Customer Base from DEER 2008 Commercial Results Review-NonUpdated Measures.xls)

Demand Reduction based on PCimpact/ECImpact x Energy Savings (from above).

Assumptions:

Manufacturer calculations and laboratory testing data place ex-ante efficiency improvements at over 30%.  See attachment ETL_Summary_Tests_7819.pdf.  This summary identifies savings under laboratory conditions as performed by the manufacturer.

Average kWh savings per unit (all vintages, based on climate zone 7) = 644.84 (simple average from worksheet)

Average kW reduction (all vintages, based on climate zone 7) = .24816

Climate Zone 7 savings are representative of all zones in the area (6, 7, 8, 10, 14, 15) due to high proportion of hotels/motels in this zone.  The program will target this measure to all climate zones and claim savings based on 70% of DEER baseline for each variation of PTAC, PTHP, climate and vintage available in the DEER NonUpdated Measures file.

Please see attached worksheet for DEER 2008 Baseline information (from NonUpdated Measures file) and associated calculations.

# Section 3. Load Shapes

11-HTL-Lodging–Hotel(GuestRooms)-COOL

# Section 4. Base Case & Measure Costs

## 4.1 Base Case Cost

Base case cost is zero, because the base case unit does not include this measure, nor do current codes require it.  It is an add-on retrofit.

## 4.2 Gross Measure Cost

Retrofit DEEMED Direct Install

Source: Revised DEER Measure Cost Summary (05_30_2008) Revised (06_02_2008).xls posted on DEER website.  Downloaded 9/30/2009.  NR – Misc & HVAC, Time clocks (heating/cooling) D08-NE-HVAC-Timeclocks.  Material Cost: $162.08, 2.50 Installation Man Hours – Retrofit, $184.11 Installation Labor Cost-Retrofit.

## 4.3 Incremental Measure Cost (For DEEMED measures only)

Retrofit DEEMED Direct Install

Source: Revised DEER Measure Cost Summary (05_30_2008) Revised (06_02_2008).xls posted on DEER website.  Downloaded 9/30/2009.  NR – Misc & HVAC, Time clocks (heating/cooling) D08-NE-HVAC-Timeclocks.  Material Cost: $162.08, 2.50 Installation Man Hours – Retrofit, $184.11 Installation Labor Cost-Retrofit.

# Attachments

# References

DEER 2011 Net-To-Gross Ratios.  (“DEER2011-NTG_IncludingCarryoversFromDEER2008_2011-12-07.xls”, accessed March 26, 2012 at http://www.deeresources.com/index).

“Technology and Measure Cost Data”  2008 Database for Energy-Efficient Resources Version 2008.2.05 December 16, 2008.  For use in the California IOU 2009-2011 Energy Efficiency Planning and Reporting.  Revised DEER Measure Cost Summary (05_30_2008).xls.

May 30, 2008. Retrieved January 18,2010 from www.deeresources.com/