Work Paper SDGE WPNRLG0006

Compact Fluorescent Fixture

Revision # 3

San Diego Gas & Electric

Energy Efficiency Engineering

Non Residential - Compact Fluorescent Fixtures

Measure Codes L-C11, L-C21, L-C31, L-C41, L-C51, L-C61

# At-a-Glance Summary

| Applicable Measure Codes: | L-C61 | L-C11 | L-C21 | L-C31 | L-C41 | L-C51 |
| --- | --- | --- | --- | --- | --- | --- |
| Measure Description: | Same as L-C11-L-C41; except must be exterior installation | Replace an existing interior incandescent, mercury vapor, T12/high output fluorescent, T12/very high output fluorescent, standard metal halide, or high pressure sodium fixture with a new compact fluorescent fixture |  |  | Same as L-C11-L-C41; except must be high bay installation |  |
| Energy Impact Common Units: | Fixture |  |  |  |  |  |
| Base Case Description: | Existing exterior standard metal halide fixture, 70W lamp | Existing interior standard metal halide fixture, 70W lamp | Existing interior standard metal halide fixture, 150 W lamp | Existing interior standard metal halide fixture 250 | Existing interior standard metal halide fixture ≥ 400W | Existing interior standard metal halide fixture ≥ 400W |
| Base Case Energy Consumption: | ≤100 Watt lamp | ≤100 Watt lamp | 101-175 Watt lamp | 176-399 Watt lamp | 400 Watt lamp | >400 Watt lamp |
| Measure Energy Consumption: | Source: SDGE Calculation |  |  |  |  |  |
| Energy Savings (Base Case – Measure) |  |  |  |  |  |  |
| Costs Common Units: | $ per Fixture |  |  |  |  |  |
| Base Case Equipment Cost ($/unit): | N/A |  |  |  |  |  |
| Measure Equipment Cost ($/unit): | Source: PGE |  |  |  |  |  |
| Measure Incremental Cost ($/unit): | Source: PGE | Source: PGE | Source: PGE | Source: PGE | Source: PGE | Source: PGE |
| Effective Useful Life (years): | Source: DEER 08 | Source: DEER 08 | Source: DEER 08 | Source: DEER 08 | Source: DEER 08 | Source: DEER 08 |
| Program Type: | Retrofit |  |  |  |  |  |
| Net-to-Gross Ratios: | Source: DEER 2011 |  |  |  |  |  |
|  | 0.53 downstream, 0.8 Direct Install |  |  |  |  |  |
| Important Comments: | None |  |  |  |  |  |

# Work Paper Approvals

|  | Date |
| --- | --- |
|  | Date |
|  | Date |

# Document Revision History

| ### Revision # | ### Date | ### Author | ### Description |
| --- | --- | --- | --- |
| 0 | March 2009 | ### Unknown | ### Adopted form PGE Compact Fluorescent Fixtures060407 and from SDGE Lighting WP_06 |
| 1 | 10/28/2009 | Lucie Sidibe | - Updated Non Residential Compact Fluorescent Fixtures - Savings Calculations to reflect DEER 2008 V2.05 Interactive effect - NTG Was Adjusted to meet Deer 2008 - Measure EUL was Adjusted to meet Deer 2008 |
| 2 | 7/29/2010 | Lucie Sidibe | - Product Code was revised to match EEBR Product Codes - General Editing was done. |
| 3 | 6-26-2012 | Charles Harmstead | Updated NTG for DEER 2011 |
|  |  | Peter Ford | Added reference to WPSDGENRLG0999 Rev0 and changed tables accordingly |

# Table of Contents

At-a-Glance Summary	i

Work Paper Approvals	ii

Document Revision History	iii

Table of Contents	iv

Section 1. General Measure & Baseline Data	5

1.1 Measure Description & Background	5

1.2 DEER Differences Analysis	6

1.3 Codes & Standards Requirements Analysis	6

1.4 Measure Effective Useful Lives and hours of operations	6

1.5 Net-to-Gross Ratios for Different Program Strategies	7

Section 2. Calculation Methods	7

2.1 Energy Savings & Demand Reduction Calculations	7

Section 3. Load Shapes	8

3.1 Base Case Load Shapes	8

3.2 Measure Load Shapes	8

Section 4. Base Case & Measure Costs	8

4.1 Base Case(s) Costs	8

4.2 Measure Costs	8

4.3 Incremental & Full Measure Costs	9

References	10

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

Catalog Description

COMPACT FLUORESCENT FIXTURES

Fixture – Refers to new equipment being installed based on system (lamp and ballast) wattage

Requirements:

- Only complete, new Compact Fluorescent fixtures qualify.

- New fixtures must not exceed the maximum ”New Fixture” wattage listed in Table below for each range of lamp wattage being replaced.

- New fixture must be equipped with pin-based Compact Fluorescent Lamps (CFL) and High Power factor (HPF) electronic ballasts.

- Must replace an existing lamp that is Incandescent, Mercury Vapor, Standard Metal Halide or High Pressure Sodium fixtures in interior installations.

- New exterior installations qualify if existing lamps are less than or equal to 100 Watts.

- May qualify for an additional control(s) rebate with an Occupancy Sensor and/or Photo-Sensor for daylight harvesting, provided all requirements are met.

- While making lamp and fixture selection customer is to insure that Initial Lumen per Watts as well as Lumen depreciation is adequate.

| Product Code | Existing Lamp Wattage | Existing Fixture Wattage (General) | New Fixture Wattage |
| --- | --- | --- | --- |
| L-C41 | Interior 400 Watt lamp | 458 Watt fixtures | ≤ 244Watt |
| L-C31 | Interior 176 - 399 Watt lamp | 215-458 Watts Fixture | ≤ 192Watt |
| L-C21 | Interior 101 - 175 Watt lamp | 128-215 Watts Fixture | ≤ 128Watt |
| L-C11 | Interior ≤ 100 Watt lamp | ≤ 128 Watts Fixture | ≤ 70 Watt |
| L-C51 | Interior ≤400 Watts lamp | 458 Watt fixtures | ≤360watts |
| L-C61 | Exterior ≤ 100 Watt lamp | ≤ 128 Watts Fixture | ≤ 70 Watt |

Program Restrictions and Guidelines

Terms and Conditions: In all cases, the Wattage of the replacement fixture must be less than the Wattage of the existing lamp.  The maximum replacement Wattage listed in the table for each category is typically associated with the highest Wattage in the base case range.  Exterior fixtures are only eligible up to a maximum of 100W.

Market Applicability: The primary market sectors for 400W and greater lamps are Warehouse, Storage, and Manufacturing.  Smaller fixtures are likely to be found in all other non-residential sectors.

Technical Description

Compact Fluorescent Fixtures are treated as a separate category from Linear Fluorescent Fixtures because of differences in lamp/ballast efficacy and equipment cost structure. This category is based on replacing existing Standard Metal Halide fixtures. Existing Pulse Start Metal Halide installations do not qualify. Existing Incandescent, Mercury Vapor, T12 HO, T12 VHO, and High Pressure Sodium fixtures with at least the same Wattage as the assumed existing Standard Metal Halide fixture also qualify. Savings for each Wattage Range are based on the most applicable Compact Fluorescent lamp/ballast combination to achieve similar light output as the assumed existing Standard Metal Halide fixtures. To qualify, Compact Fluorescent Fixtures must have a maximum Wattage as stipulated in the catalog description and less than the fixture being replaced.

## 1.2 DEER Differences Analysis

DEER methodology was followed in developing energy savings, with Interactive effects taken from the DEER 2011 READI tool.

## 1.3 Codes & Standards Requirements Analysis

In Section 149(b) of California’s Title 24 2008 Non-Residential Building Energy Efficiency Standards, the Alteration codes and standards language states:

- Alterations to existing indoor lighting systems shall meet the following requirements:

1. Alterations that increase the connected lighting load, replace, or remove and re-install a total of 50 percent or more of the luminaires in an enclosed space, shall meet the requirements of Sections 130 and 146; and

2. The following wiring alterations shall meet the requirements of Sections 119, 131, and 134:

i. Where new or moved wiring is being installed to serve added or moved luminaires; or

ii. Where conductor wiring from the panel or from a light switch to the luminaires is being replaced, or

iii. Where a lighting panel is installed or relocated.

3. For an alteration where an existing enclosed space is subdivided into two or more spaces, the new enclosed spaces shall meet the requirements of Sections 131(a) and (d); and

4. Alterations that have less than 0.5 watts per square foot and increase the existing lighting power density to 0.5 watts per square foot or greater shall meet the requirements of Sections 119, 130, 131, 134,143(c), and 146.

Title 24 revisions have been approved, however, are not yet in effect for 2012.  This measure is not affected by the either the 2008 or 2012 Title 24 modifications for alteration above code requirements since the measure only involves replacing lamps and is not replacing the housing of the existing fixture nor is it increasing the connected lighting load.

## 1.4 Measure Effective Useful Lives and hours of operations

Interior Fixtures (L-C11-L-C51)

Based on DEER 2011 updated EUL table the Effective Useful Life (EUL) of the interior CFL Fixtures is 12 years.

L- C61 (Exterior fixture) Hours of Operation

The hours of lighting operation are assumed to be 4,100hours for all building types, based on PG&E’s PY 2004/2005 lighting working papers

(This information was obtain in the 2004/2005 DEER Update Study by Itron)

## 1.5 Net-to-Gross Ratios for Different Program Strategies

Table-2 below shows the Net-to-Gross ratio for this measure, this information was obtained from the DEER 2011 NTGR table

Table-2: Net-to-Gross Ratio

| Delivery Method | Program Name | NTG |
| --- | --- | --- |
| NonRes-sAll-mCFL-dn | EEBR | .53 |
| NonRes-sAll-mCFL-dir | Direct Install | .8 |

# Section 2. Calculation Methods

# 2.1 Energy Savings & Demand Reduction Calculations

The base case lamp and fixture wattage was taken form the SDGE Standard Fixture Wattage table.  For  ∆ Watt values, reference is made to WPSDGENRLG0999 which contains a complete table of lighting measures for SDG&E.

Table 1:  Base Case Wattages Assumptions

| SDGE Measure ID | Base case Description/Wattage | Measure Description/Wattage | ∆ Watt ( Base Wattage- Measure Wattage) |
| --- | --- | --- | --- |
| L-C11 | Lamp : 70 W Standard MH | Interior Fixture: ≤70Watts | See WPSDGENRLG0999 |
|  | Fixture Wattage: 95 W |  |  |
| L-C21 | Lamp: 150 W Standard MH | Interior Fixture :128 Watts | See WPSDGENRLG0999 |
|  | Fixture Wattage: 190 W |  |  |
| L-C31 | Lamp wattage: 250 W | Interior Fixture: 192Watts | See WPSDGENRLG0999 |
|  | Fixture Wattage: 295 W |  |  |
| L-C41 | Lamp wattage: 400 W | Interior Fixture: 244 Watts | See WPSDGENRLG0999 |
|  | Fixture Wattage: 458 W |  |  |
| L-C51 | Lamp Wattage:400W Fixture Wattage: 458 W | Interior Fixture: ≤360 Watts | See WPSDGENRLG0999 |
| L-C61 | Lamp : 70 W Standard MH | Exterior Fixture : ≤70Watts | See WPSDGENRLG0999 |
|  | Fixture Wattage: 95 W |  |  |

Energy Savings kWhunit ⋅ year=(ΔWatts/unit)×(Annual hours of use)×(Interactive Effects)1,000 Watt hours/kWh   Equation 1

Demand Reduction [kW/Unit] = (∆Watts/unit) x (Peak Coincident Factor) x (Interactive Effects)	Equation 2

1,000 Watts / kW

Gas Savings  Thermunit ⋅ year= (∆Watts/unit) x (annual hours of use) x (3.413 BTU/Watt hours) x Interactive Effects   Equation 3

100,000 (BTU/Therm)

For saving calculation and interactive effect methodology, as well as dual baseline, EUL, and RUL considerations, refer to the embedded spreadsheet contained in WPSDGENRLG0999.

# Section 3. Load Shapes

## 3.1 Base Case Load Shapes

The base case load shape for all measures would be expected to follow a typical non-residential lighting end use load shape.

## 3.2 Measure Load Shapes

For purposes of the net benefits estimates in the E3 calculator, what is required is the load shape that ideally represents the difference between the base equipment and the installed energy efficiency measure.  This difference load profile is what is called the Measure Load Shape and would be the preferred load shape for use in the net benefits calculations.

The measure load shape for these measures is determined by the E3 calculator based on the applicable non-residential market sector and lighting end-use

- Section 4. Base Case & Measure Costs

## 4.1 Base Case(s) Costs

There are no costs associated with the base case because these measures are eligible in retrofit (RET) applications only.

## 4.2 Measure Costs

All labor costs and equipment costs were adopted form PGE work paper/Documentation (PGE Work paper PGECOLTG131) the labor cost is assumed to be the same across all measures.  The labor cost is $120 to remove an existing fixture and install a new fixture.  Equipment costs vary across fixture size.

L-C61/L-C11: $140

The equipment cost for a new fixture equipped with a 60W CFL and electronic ballast is assumed to be similar to the cost of a new fixture with an 85 W CFL and ballast – $140.

L-C21: $180

The equipment cost for a new fixture equipped with four 32W CFLs and electronic ballasts is $180.

L-C31:$180

The equipment cost for a new fixture equipped with two 96W CFLs and electronic ballasts is $180

L-C41/L-C51: $180

The equipment cost for a new fixture equipped with two 120W CFLs and electronic ballasts is $180.

## 4.3 Incremental & Full Measure Costs

- This measure is offered as RET only and therefore only full measure (installed) cost is applicable.

- Installed cost (Full) = Measure Equipment Cost + Labor Cost

LC61/L-C11: $260

- Installed cost (Full) = $140 + $120=$260

L-C21: $300

- Installed cost (Full) = $180 + $120=$300

L-C31: $300

- Installed cost (Full) = $180 + $120=$300

L-C41/L-C51: $320

- Installed cost (Full) = $200 + $120=$320

- References

The following references are provided:

- DEER 2011 Net-To-Gross Table

- Appendix B: Table of Standard Fixture Wattages

- 2004/2005 Deer Update Study