Workpaper SDGENRRN0010

New Display Cases with Doors

Revision #1

San Diego Gas & Electric

Energy Efficiency Engineering

New Refrigeration Display Cases with Doors

Measure Codes R-C11 and R-C21

### Core Measure Summary Table

| General Measure Information |  |  |  |  |  |  |  | PT |  | 1st Baseline Period |  |  |  | 2nd Baseline Period |  |  |  | TOU |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure Name | Measure RunID | Solution Code | CZ | Building Type | Load Shape | EUL | Unit Definition | Program Type (NEW, ROB, RET) | Applicable Code | Gross Unit Annual Electricity Savings (kWh/unit) | User Entered kW Savings per unit (kW/unit) | Gas Savings (Therms) | 1st Baseline Useful Life | kWh Saving per unit (kWh/unit) | kW Savings per unit (kW/unit) | Gas Savings (Therms) | 2nd Baseline Useful Life | % TOU |
| Medium Temperature Reach-in Display Case | To be Exported from the MMDB | RF-68765 | 06 | Assembly | Refrigeration | 12.0 | Linear Foot | RET | No | 114.52 | 0.03 | 25.55 | 12.00 | N/A | N/A | N/A | 0.00 | 0.00 |
| Medium Temperature Reach-in Display Case | To be Exported from the MMDB | RF-68765 | 07 | Assembly | Refrigeration | 12.0 | Linear Foot | RET | No | 104.36 | 0.03 | 23.23 | 12.00 | N/A | N/A | N/A | 0.00 | 0.00 |
| Medium Temperature Reach-in Display Case | To be Exported from the MMDB | RF-68765 | 08 | Assembly | Refrigeration | 12.0 | Linear Foot | RET | No | 111.89 | 0.01 | 19.81 | 12.00 | N/A | N/A | N/A | 0.00 | 0.00 |
| Medium Temperature Reach-in Display Case | To be Exported from the MMDB | RF-68765 | 09 | Assembly | Refrigeration | 12.0 | Linear Foot | RET | No | 107.99 | 0.10 | 18.03 | 12.00 | N/A | N/A | N/A | 0.00 | 0.00 |
| Medium Temperature Reach-in Display Case | To be Exported from the MMDB | RF-68765 | 10 | Assembly | Refrigeration | 12.0 | Linear Foot | RET | No | 117.63 | 0.07 | 18.35 | 12.00 | N/A | N/A | N/A | 0.00 | 0.00 |
| Medium Temperature Reach-in Display Case | To be Exported from the MMDB | RF-68765 | 13 | Assembly | Refrigeration | 12.0 | Linear Foot | RET | No | 157.96 | 0.09 | 19.55 | 12.00 | N/A | N/A | N/A | 0.00 | 0.00 |
| Medium Temperature Reach-in Display Case | To be Exported from the MMDB | RF-68765 | 14 | Assembly | Refrigeration | 12.0 | Linear Foot | RET | No | 210.74 | 0.05 | 19.70 | 12.00 | N/A | N/A | N/A | 0.00 | 0.00 |
| Medium Temperature Reach-in Display Case | To be Exported from the MMDB | RF-68765 | 15 | Assembly | Refrigeration | 12.0 | Linear Foot | RET | No | 75.87 | 0.004 | 11.59 | 12.00 | N/A | N/A | N/A | 0.00 | 0.00 |

Note: For the complete list of Measures, refer to the attached calculation spreadsheet

### Costing and NTG Summary Table

| General Measure Information |  |  |  | PT |  | NTG |  |  | IR | 1st Baseline Period | 2nd Baseline Period | IMC | DIM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure Name | Solution Code | CZ | Unit Definition | Program Type (NEW, ROB, RET) | Applicable Code | NTG Non-Res. | NTG Res. | NTG Multi Family | NTG Non-Res. | Gross Measure Cost per unit | Gross Measure Cost per unit | Incremental Measure Cost per unit | Delivery & Incentive Method |
| Medium Temperature Reach-in Display Case | RF-68765 | 6 | Linear Foot | RET | No | 0.60 | N/A | N/A | 1.00 | $855.41 | N/A | $855.41 | Financial Support / Down-Stream Incentive - Deemed |
| Medium Temperature Reach-in Display Case | RF-68765 | 7 | Linear Foot | RET | No | 0.60 | N/A | N/A | 1.00 | $898.99 | N/A | $898.99 | Financial Support / Down-Stream Incentive - Deemed |
| Medium Temperature Reach-in Display Case | RF-68765 | 8 | Linear Foot | RET | No | 0.60 | N/A | N/A | 1.00 | $886.06 | N/A | $886.06 | Financial Support / Down-Stream Incentive - Deemed |
| Medium Temperature Reach-in Display Case | RF-68765 | 9 | Linear Foot | RET | No | 0.60 | N/A | N/A | 1.00 | $930.74 | N/A | $930.74 | Financial Support / Down-Stream Incentive - Deemed |
| Medium Temperature Reach-in Display Case | RF-68765 | 10 | Linear Foot | RET | No | 0.60 | N/A | N/A | 1.00 | $860.70 | N/A | $860.70 | Financial Support / Down-Stream Incentive - Deemed |
| Medium Temperature Reach-in Display Case | RF-68765 | 13 | Linear Foot | RET | No | 0.60 | N/A | N/A | 1.00 | $826.78 | N/A | $826.78 | Financial Support / Down-Stream Incentive - Deemed |
| Medium Temperature Reach-in Display Case | RF-68765 | 14 | Linear Foot | RET | No | 0.60 | N/A | N/A | 1.00 | $829.76 | N/A | $829.76 | Financial Support / Down-Stream Incentive - Deemed |
| Medium Temperature Reach-in Display Case | RF-68765 | 15 | Linear Foot | RET | No | 0.60 | N/A | N/A | 1.00 | $879.10 | N/A | $879.10 | Financial Support / Down-Stream Incentive - Deemed |

Note: For the complete list of Measures, refer to the attached calculation spreadsheet

# Document Revision History

| Revision # | MM/DD/YY | Author/Affiliation | Summary of Changes |
| --- | --- | --- | --- |
| 1 | August 30, 2012 | Max Twogood SDG&E | Rev 0 retired. Work Paper adopted from PGE Work Paper: “PGECOREF104 R4 Display Cases with Doors.doc” Removed Direct Install Net-To-Gross, as this is not an SDG&E DI measure. Updated summary table with savings and costs from attachments in Appendix A for Climate Zones 6, 7, 10, 14, 15 in SDG&E territory. Measure codes on title page were updated to match applicable measure codes in SDG&E’s deemed program, EEBR |

# Section 1. General Measure & Baseline Data

## 1.1  Measure & Delivery Description

### 1.1a Measure Description

This work paper discusses the replacement of old open vertical (or multi-deck) low-temperature (LT) and medium-temperature (MT) display cases with reach-in glass door display cases. These types of display cases can be found in small- and medium-to-large size grocery stores. Medium-temperature display cases are used to stock dairy, deli, fish and meat. Low-temperature display cases are used to stock frozen food and ice cream. The air temperature inside medium temperature display cases can range from +24°F to +38°F, and the air temperature inside low temperature display cases is up to  -5°F [A]. Since the majority of the losses are due to infiltration this work paper only considers infiltration losses.

Table 1 Measure Names

| Solution Code | Measure name |
| --- | --- |
| RF-68765 | Medium Temperature Reach-in Display Case |
| RF-75389 | Low Temperature Reach-in Display Case |

### 1.1b Delivery and Incentive Mechanism

This work paper addresses retrofit (RET) installations of the new MT and LT display cases with doors. The delivery methods are: Financial Support - Down Stream Incentive – Deemed, Financial Support – On-bill Finance – loan, Financial Support – Direct Install, Partnership – Down-Stream Incentive – Deemed, and Partnership – On-bill Finance – Loan.

### 1.1c Measure Requirements

Salvage, disposal or photographic records of replaced equipment are required as part of program application requirements when early replacement or open-to-closed case conversion savings are being utilized to ensure the correct baseline is assumed for these measures.

Display case replacements that are part of large-scale store remodels and any new construction projects should be revised to be customized measures and should not utilize this work paper. Large-scale remodels are defined as any project involving 50% of the linear feet of refrigerated casework or 32 linear feet of casework replacements, whichever is less.

The measures in this work paper are appropriate for all California climate zones as well as all the building types shown in Section 3.

Express Requirements

The rebates for these measures are a part of the Express program. To qualify for the incentive, the following requirements must be met:

- The retrofit must involve the replacement of an existing open multi-deck display case door with a new high-efficiency reach-in unit with double-pane glass doors with heat-reflective treatment or gas fill, ECM fan motors (evaporator and/or condenser), and T8 lamps and electronic ballast. This solution can be applied to self-contained or remote cases. The display case temperature setpoint must be between 5 and 24 degrees Fahrenheit for low-temp cases and between 24 and 36 degrees Fahrenheit for med-temp cases.

- The display cases must be properly measured. New display cases are incentive based on linear footage of new display case.

- The new case length must be equal to or shorter than the original case.

- Exclusions: Deli cases, custom coolers/freezers, and walk-in boxes with reach-in doors do not qualify.

Pacific Gas and Electric

Requirements:

- Installation address must have a commercial electric account with PG&E.

- Must replace an existing, open, multi-deck, display case with a new, high-efficiency, reach-in unit with standard glass doors with an Electronically Commutated Motor (ECM) fan, T-8 lamps and an electronic ballast.

- New case length must be equal to, or shorter than, the original case.

- This measure is for remote cases only.

- Rebate is based on linear footage of new display case.

- Exclusions: Deli cases, custom coolers/freezers and walk-in boxes with reach-in doors do not qualify.

## 1.2  DEER Differences Analysis

Measure ID D03-207 in the Database for Energy Efficient Resources (DEER) addresses replacing old vertical (or multi-deck) medium-temperature display cases with medium-temperature display cases with glass doors [26]. However, it does not address replacing old vertical (or multi-deck) low-temperature display cases with low-temperature display cases with glass doors. DEER 2008, however, does not include this measure. For medium-temperature display cases, this work paper uses DEER 2011 values extracted with the READI tool and applies vintage weighting factors obtained from DEER2008 Commercial Building weights.

For a discussion of the appropriate effective useful life, see Section 1.4, and for a discussion of the appropriate net-to-gross ratio, see Section 1.5.

Table 2 DEER Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | No |
| Scaled DEER Measure | No |
| DEER Building Prototypes Used | Yes |
| Deviation from DEER | DEER does not include retrofitting old vertical low-temperature display cases with low-temperature display cases with glass doors. |
| DEER Version | DEER 11, DEER 05 |
| DEER Run ID and Measure Name (Sample) | D03-207 |

## 1.3  Code Analysis

This measure is not governed by either State or Federal code and standards, such as California Title 24 (2008) [208] and Title 20 (2010) [277].

Table 3 Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| Title 20 (2010) | N/A | N/A |
| Title 24 (2008) | N/A | N/A |

## 1.4  Measure Effective Useful Life

DEER11 documentation provides EUL and RUL information to be used for the 13-14 program cycle on www.deeresources.com. The DEER documentation “Summary of EUL-RUL Analysis for the April 2008 Update to DEER” provides the RUL value as a flat 1/3 of the EUL value. The RUL value will only be applied to the first baseline period for retrofit measures that have applicable code that will affect the energy savings. In all other installation types and retrofit with no applicable code that affects the energy savings, the RUL is not applicable to either the first or second baseline period.

To obtain the EUL value the DEER11 documentation, EUL_Summary_10-1-08.xls [213], was consulted. Table 4 below identifies the value/methodology used for the measures in this work paper.

Table 4 DEER08 EUL Value/Methodology

| Market | Enduse | Measure | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- |
| Non-Residential | Refrigeration | Zero Heat Reach-in Glass Doors | 12 | N/A |

## 1.5  Net-to-Gross Ratios for Different Program Strategies

The NTG value was obtained from the “DEER2011_NTGR_2012-05-16.xls” on the DEER website as required by Version 4 of the California Public Utilities Commission (CPUC) Energy Efficiency Policy Manual [132]. The relevant NTGR for this measure is shown in Error: Reference source not found below.

Table 5 Net-to-Gross Ratio

| NTGR_ID* | Description* | Sector* | BldgType* | ProgDelivID | NTG* |
| --- | --- | --- | --- | --- | --- |
| Com-Default>2yr | All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | Com | Any | All | 0.6 |

*Denotes that the column is taken from the DEER NTG Table.

The installation rate (IR) is identified in the calculation attachment. This value is obtained from a spreadsheet created by the DEER team titled “GrossSavingsAdjustments.xlsx”. The installation rate varies by end use, sector, technology, application, and delivery method.

## Spillage rate will also be applied to measures however the values will not be tracked in the work papers. The spillage rate will be tracked in an external table to be supplied to the Energy Division.

## 1.6  Time-of-Use Adjustment Factor

As directed by the CPUC in decision 06-06-063 dated June 29, 2006, time-of-use (TOU) adjustment factors are to be applied for residential A/C and commercial A/C (packaged and split-system direct-expansion cooling) measures only. Since this is not an A/C measure, the TOU adjustment factor is 0. Additionally, if a measure is assigned a DEER08 load shape, i.e. the load shape starts with “DEER:” the TOU assigned to that measure should also be zero.

Table 6  TOU Summary Table

| Measure | % |
| --- | --- |
| Medium Temperature Reach-in Display Case | 0 |
| Low Temperature Reach-in Display Case | 0 |

*Note:  Check Section 3 if a measure appears to require a non-zero percentage but is assigned zero. If the load shape is a DEER08 load shape, a TOU of 0 is correct.

# Section 2. Energy Savings & Demand Reduction Calculations

The following assumptions were made for the calculations of this work paper:

- The building simulation models were generated for a Grocery Store with multiplex-compressor systems for the refrigeration display cases. Since single-compressor systems are less efficient than multiplex-compressor systems, only multiplex systems have been analyzed as a conservative estimate of savings. According to the DEER Report [26], single-compressor systems were typically designed prior to 1980. To be conservative, it is assumed that the generated energy savings of this work paper will also be applied to display cases with single-compressor systems.

- This work paper is applied to display cases located inside a space which has space heating and space cooling. The unit energy savings is represented per linear-foot of the display case. The resulting savings are from refrigeration load reduction and space heating load reduction. Note that there is also a slight increase to the space cooling energy consumption. The building simulation models were generated for a Grocery Store. Since the heat gain to a display case mainly depends on the temperature maintained for the display case and the surrounding space temperature, it is assumed that the building types would not have significant impact on the energy savings. Thus, the resulting savings of Grocery Store is applied to all other building types considered in this work paper with building vintage weights.

The energy savings and demand reduction for this work paper is based on replacing the existing open vertical (multi-deck) low temperature and medium temperature display cases with reach-in glass door display cases. The display cases are applicable to, but not limited to, grocery stores. The base case display cases are replaced with similar display cases with glass doors. Additional case lighting is added to improve product visibility. Replacing open display cases with reach-in glass door display cases will reduce the infiltration load significantly, resulting in savings on the refrigeration cooling load and space heating load.

The New Medium Temperature Refrigeration Display Case with Doors measure of this work paper is addressed in the 2004-2005 Database for Energy Efficiency Resources (DEER) Update Study final Report of measure ID D03-207 [26]. Please refer to the DEER Report Section 6 for details of DEER Building Prototypes generated by eQuest 3.56, DEER 2.1 version (a graphical interface to DOE-2.2), Section 7.3 for general description for grocery refrigeration measures, and Page 7-75 for detail descriptions of this measure. The unit energy savings of this measure is obtained from READI, a DEER2011 Database Tool. The DEER measure ID D03-207 replaces existing medium temperature multi-deck cases with new cases having glass doors. The new case is assumed to have standard doors, ECM motors, T8/EB lighting.

The measures are weather sensitive and the building energy simulation tool eQuest 3.56, DEER 2.1 version was used to determine the annual impacts. The built-in, DEER building prototypes of grocery store were used for simulations of the other measure: New Low Temperature Refrigeration Display Case with Doors. The DEER building prototypes consider multiplex-compressor systems as the refrigeration type. The DEER building prototypes have built-in refrigeration fixtures for low temperature vertical display cases with doors. These fixtures were used as the measure models for the New Low Temperature Refrigeration Display Case with Doors measure simulations. Since no built-in refrigeration fixtures are available for low temperature open vertical display cases within the DEER prototype building, the baseline models were generated by modifying the built-in low temperature vertical display cases with doors into low temperature open vertical display cases. Components of the low temperature vertical display case in the baseline models and measure models are included in Table 7 below.

Table 7 Summary of Modeled Low Temperature Vertical Display Cases

| Component | VOPL Values£ (Baseline Model) | VTDL Values££ (Measure Model) |
| --- | --- | --- |
| Evaporator Fan Power | 0.0251 (kW/ft) * | 0.055 (kW/dr) |
| Lighting Power | 0.0199 (kW/ft) * | 0.076 (kW/dr) |
| Anti-Sweat Power | 0.05 (kW/ft) | 0.214 (kW/dr) |
| Infiltration Load | 1303.5 (Btu/hr-ft) | 10.46 (Btu/hr-dr) |
| Conduction Load | 248.8 (Btu/hr-ft)* | 600 (Btu/hr-dr) |
| Total Line-Up Length | 281 (ft) | 109 (doors) |

VOPL = low temperature vertical open display case; VTDL = low temperature vertical display case with transparent doors

£ Source:  DOE 2009a, Appendix D [B].

££ Built-in fixtures from DEER building prototype of a grocery store. All values are provided from the prototype.

* Average value of all efficiency levels considered for low temperature open vertical display cases.

Once the base case and measure case model simulations were completed, the energy savings and demand reduction could be determined. Comparing the total energy consumption (electricity and natural gas) of both models, the total energy savings were determined. The unit energy savings, in kWh/yr-ft for electricity and therm/yr-ft for natural gas, were calculated by dividing the total energy savings by the total line-up length of the display cases. According to the eQuest built-in models, each glass door is about 2.6 ft in length. Therefore, the total line-up length of these display case was converted by 2.6 ft per door.

Since the eQuest Refrigeration version does not have the add-on function for exporting hourly reports, the monthly peak demand outputs were utilized based on the month for the DEER defined peak demand days (during specific summer weekday periods delineated by climate zone, as set forth in CPUC Decision D06-06-063). Note that when the DEER peak period of the climate zone that was split between two months, the month that had a higher peak demand was used since it was assumed that the ambient temperature was higher for this month. The measure results were subtracted from the baseline results to determine the demand reduction. Similar to the energy savings the unit demand reduction, in kW/ft, was calculated by dividing the total demand reduction by the total line-up length of the display cases.

For medium temperature display cases, the energy savings per climate zone and vintage was extracted from DEER 2011 through the READI tool. These numbers were then vintage weighted using the DEER2008 Commercial Building weights.

Once the unit energy savings and demand reduction were determined for both low (simulated) and medium (DEER 2011) temperature display cases for each vintage and climate zone, the weighted average savings for each climate zone was determined for each building type. DEER2008 Commercial Building Weights per vintages were used to calculate the weighted average savings for each climate zone. The weighted average savings were calculated for the following building types: Assembly, Grocery, Restaurant-Sit Down, Restaurant-Fast Food, Retail-Multistory Large, Retail-Single-Story Large, and Retail-Small. The weighted average savings of all the aforementioned building types were calculated for all climate zones associated with each of the following three utility companies: Southern California Edison (SCE), Pacific Gas and Electric (PGE), and San Diego Gas & Electric (SDGE). Savings summary for all utility companies can be seen in Attachment A.

# Section 3. Load Shapes

The difference between the base case load shape and the measure load shape would be the most appropriate load shape; however, only end-use profiles are available. Therefore, the closest load shape chosen for this measure is the Refrigeration load shape. See Table 8 for a list of all Building Types and Load Shapes. See the KEMA report [31] for a more thorough discussion regarding the load shapes for this measure. The closest load shape chosen

Table 8 Building Types and Load Shapes

| Building Type | E3 Alt. Building Type | Load Shape |
| --- | --- | --- |
| Assembly | Assembly | Refrigeration |
| Grocery | Grocery_Store | Refrigeration |
| Food Store | Food_Store | Refrigeration |
| Restaurant - Fast-Food | Fast_Food_Restaurant | Refrigeration |
| Restaurant - Sit-Down | Sit_Down_Restaurant | Refrigeration |
| Retail - Multistory Large | Retail - Multistory Large | Refrigeration |
| Retail - Single-Story Large | Retail - Single-Story Large | Refrigeration |
| Retail - Small | Retail - Small | Refrigeration |

# Section 4. Base Case & Measure Costs

## 4.1 Base Case Cost

The base case cost for this measure directly references DEER 2005 [26]. According to DEER there is no cost ($0.00 per unit) associated with the base case.

## 4.2 Gross Measure Cost

According to the DEER 2011 cost documentation [215], the equipment cost is $574.87 per linear foot with a labor cost of $331.41 per linear-ft of new MT display cases with doors. Because LT display cases with doors does not appear in DEER 2011, a review of manufacturers’ data and invoices submitted to the Express Efficiency program in 2007 revealed equipment cost of $493.13 per linear-ft of LT fixture [C]. Assuming that there are no differences in labor cost for installing low- or medium-temperature display cases, the same labor cost for MT fixtures reported by DEER 2011 ($331.41 per linear-ft of fixture) is applied to LT fixtures. Table 9 summarizes the cost data.

For RET, Gross Measure Cost (GMC) is represented by the equation below:

GMC = Measure Equipment Cost + Measure Labor Cost

Table 9 Labor and Equipment Costs for Low- and Medium-temperature Display Cases

| Case Classification | Unit | Labor | Equipment | Total |
| --- | --- | --- | --- | --- |
| Low-temperature | per linear-ft of display case | $331.41 | $493.13 | $824.54 |
| Medium-temperature | per linear-ft of display case | $331.41 | $574.87 | $906.28 |

The cost of both the low-temperature and medium-temperature display cases with doors requires climate zone multipliers. The complete Gross Measure Cost with the climate zone multiplier factored in for each climate zone is shown in the Attachment 1 Excel file in the Attachments section.

## 4.3 Incremental Measure Cost

For this measure category, the incremental measure cost(IMC) is used strictly for providing insight to program managers to assist in determining rebates for deemed measures. For retrofit measures the incremental measure cost is NOT used for reporting in the cost effectiveness calculations.

Incremental Measure Cost is the premium cost to install an energy efficient measure over a standard efficiency measure or code baseline measure. While IMC has a straight forward definition, depending on the install type the equation does vary. The incremental cost is only used to help determine program incentives. It is not affected by the first and second baseline periods and may differ from the cost used for cost effectiveness calculations.

For NEW, ROB, and RET measures, there exists a theoretical base case that the measure can be compared to in cost. Because a base case exists for NEW, ROB, and RET, IMC is represented by the equation below:

IMC 	= (Measure Equipment Cost + Measure Labor Cost) –

(Base Case Equipment Cost + Base Case Labor Cost)

*Note: Unless stated otherwise the measure case labor and base case labor are assumed to be the same value reducing the equation to the following:

IMC 	= Measure Equipment Cost – Base Case Equipment Cost

The incremental measure cost (IMC) is the measure material cost minus the base material cost or ($493.13-$0) for low-temperature display cases and ($574.87-$0) for medium temperature display cases and turns out to be $493.13 for the low temperature display cases and $574.87 for the medium temperature display cases.

# Attachments

# References

[26]

[31]

[132]

[208]

[213]

[215]

[277]

_________

[A] ASHRAE 2006. Refrigeration Handbook. Atlanta, Georgia. pp. 46.2, Table 1.

[B] DOE 2009a. Energy Conservation Standards for Commercial Refrigeration Equipment:

Technical Support Document, U.S. Department of Energy, January 2009,

http://www1.eere.energy.gov/buildings/appliance_standards/commercial/refrig_equip_final_rule.html

[C] SCE’s 2007 Express Efficiency Program: Survey of Customer Invoices. September 2007.