Workpaper WPSDGENRRN0110

Auto-Closers for Main Doors

Revision 0

San Diego Gas & Electric

Energy Efficiency Engineering

Auto-Closers for Main Cooler or Freezer Doors

# At-A-Glance Summary

| Applicable Measure Codes: | R79 | R80 |
| --- | --- | --- |
| Measure Description: | This measure installs an automatic door closer for a walk-in cooler. The measure must be applied to an insulated opaque door such that the door will close when it is within one inch of full closure. | This measure installs an automatic door closer for a walk-in freezer. The measure must be applied to an insulated opaque door such that the door will close when it is within one inch of full closure. |
| Energy Impact Common Units: | $ Per Closer. | $ Per Closer. |
| Base Case Description: | Cooler without auto-closer installed on door. | Freezer without auto-closer installed on door. |
| Base Case Energy Consumption: | Source: DEER 2005: D03-208 Depends on climate zone and vintage. | Source: DEER 2005: D03-209 Depends on climate zone and vintage. |
| Measure Energy Consumption: | Source: DEER 2005: D03-208 Depends on climate zone and vintage. | Source: DEER 2005: D03-209 Depends on climate zone and vintage. |
| Energy Savings (Base Case – Measure) | Source: DEER 2005: D03-208 Depends on climate zone and vintage. | Source: DEER 2005: D03-209 Depends on climate zone and vintage. |
| Costs Common Units: | $ Per closer. | $ Per closer. |
| Base Case Equipment Cost ($/unit): | $0 | $0 |
| Measure Equipment Cost ($/unit): | Source: DEER2008, 2June08 $120.00 per closer | Source: DEER2008, 2June08 $120.00 per closer |
| Measure Incremental Cost ($/unit): | Source: DEER 2008 $156.82 per closer | Source: DEER 2008 $156.82 per closer |
| Effective Useful Life (years): | Source: DEER2008, 1Oct08: D03-208 8 years. | Source: DEER2008, 1Oct08: D03-208 8 years. |
| Program Type: | Retrofit and New Construction | Retrofit and New Construction |
| Net-to-Gross (NTG) Ratio: | Source: DEER 2011 | Source: DEER 2011 |
| Important Comments: | Excludes interactive effects; walk-ins reject heat to the exterior and should not effect the HVAC system. | Excludes interactive effects; walk-ins reject heat to the exterior and should not effect the HVAC system. |

# At-A-Glance Measure List

| Measure Code | DEER RunID | Measure Description | Building Type | Building Vintage | Climate Zone | Peak Electric Demand Reduction (kW/Closer) | Electric Savings (kWh/ Closer) | Gas Savings (therms/ Closer) | Base Case Cost | Measure Cost | Measure Incremental Cost | Effective Useful Life (years) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  | ($/Closer) | ($/Closer) | ($/Closer) |  |
| R79 | CGro0103GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 3 | Z01 | 0.079 | 901.95 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0105GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 5 | Z01 | 0.095 | 838.48 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0175GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 75 | Z01 | 0.159 | 1007.88 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0185GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 85 | Z01 | 0.127 | 1018.88 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0196GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 96 | Z01 | 0.063 | 956.73 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro01NWGMCAC | Install automatic door closer on walk-in cooler doors | BCR | NW | Z01 | 0.095 | 839.27 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | N/A | Install automatic door closer on walk-in cooler doors | BCR | OTR | Z01 | 0.095 | 838.48 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0203GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 3 | Z02 | 0.143 | 930 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0205GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 5 | Z02 | 0.127 | 857.07 | 0 | $0 | $120.00 | $156.82 | 8 |

| R79 | CGro0275GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 75 | Z02 | 0.095 | 1073.8 | 0 | $0 | $120.00 | $156.82 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| R79 | CGro0285GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 85 | Z02 | 0.286 | 1063.13 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0296GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 96 | Z02 | 0.159 | 974.95 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro02NWGMCAC | Install automatic door closer on walk-in cooler doors | BCR | NW | Z02 | 0.127 | 862.25 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | N/A | Install automatic door closer on walk-in cooler doors | BCR | OTR | Z02 | 0.127 | 857.07 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0303GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 3 | Z03 | 0.175 | 914.55 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0305GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 5 | Z03 | 0.095 | 845.77 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0375GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 75 | Z03 | 0.127 | 1037.88 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0385GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 85 | Z03 | 0.127 | 1020.98 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0396GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 96 | Z03 | 0.111 | 970.66 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro03NWGMCAC | Install automatic door closer on walk-in cooler doors | BCR | NW | Z03 | 0.095 | 846.32 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | N/A | Install automatic door closer on walk-in cooler doors | BCR | OTR | Z03 | 0.095 | 845.77 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0403GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 3 | Z04 | 0.111 | 937.13 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0405GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 5 | Z04 | 0.111 | 862.54 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0475GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 75 | Z04 | 0.159 | 1057 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0485GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 85 | Z04 | 0.206 | 1067.71 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0496GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 96 | Z04 | 0.127 | 979.82 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro04NWGMCAC | Install automatic door closer on walk-in cooler doors | BCR | NW | Z04 | 0.095 | 861.7 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | N/A | Install automatic door closer on walk-in cooler doors | BCR | OTR | Z04 | 0.095 | 861.7 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0503GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 3 | Z05 | 0.127 | 912.04 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0505GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 5 | Z05 | 0.079 | 851.07 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0575GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 75 | Z05 | 0.27 | 1036.63 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0585GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 85 | Z05 | 0.222 | 1041.84 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro0596GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 96 | Z05 | 0.127 | 962.64 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro05NWGMCAC | Install automatic door closer on walk-in cooler doors | BCR | NW | Z05 | 0.095 | 851.82 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | N/A | Install automatic door closer on walk-in cooler doors | BCR | OTR | Z05 | 0.079 | 851.07 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1103GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 3 | Z11 | 0.127 | 972.43 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1105GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 5 | Z11 | 0.143 | 899.21 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1175GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 75 | Z11 | 0.159 | 1106.75 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1185GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 85 | Z11 | 0.238 | 1088 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1196GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 96 | Z11 | 0.127 | 1005.38 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro11NWGMCAC | Install automatic door closer on walk-in cooler doors | BCR | NW | Z11 | 0.111 | 902 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | N/A | Install automatic door closer on walk-in cooler doors | BCR | OTR | Z11 | 0.143 | 899.21 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1203GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 3 | Z12 | 0.159 | 938.89 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1205GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 5 | Z12 | 0.111 | 888.32 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1275GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 75 | Z12 | 0.19 | 1080.32 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1285GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 85 | Z12 | 0.175 | 1098.89 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1296GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 96 | Z12 | 0.111 | 984.09 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro12NWGMCAC | Install automatic door closer on walk-in cooler doors | BCR | NW | Z12 | 0.127 | 886.66 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | N/A | Install automatic door closer on walk-in cooler doors | BCR | OTR | Z12 | 0.127 | 886.66 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1303GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 3 | Z13 | 0.175 | 981.32 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1305GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 5 | Z13 | 0.175 | 917.05 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1375GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 75 | Z13 | 0.143 | 1132.75 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1385GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 85 | Z13 | 0.159 | 1137.91 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1396GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 96 | Z13 | 0.095 | 1005.89 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro13NWGMCAC | Install automatic door closer on walk-in cooler doors | BCR | NW | Z13 | 0.111 | 924.61 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | N/A | Install automatic door closer on walk-in cooler doors | BCR | OTR | Z13 | 0.175 | 917.05 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1603GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 3 | Z16 | 0.19 | 890.93 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1605GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 5 | Z16 | 0.111 | 823.98 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1675GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 75 | Z16 | 0.111 | 1032.29 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1685GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 85 | Z16 | 0.143 | 1025.89 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro1696GMCAC | Install automatic door closer on walk-in cooler doors | BCR | 96 | Z16 | 0.19 | 942.71 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | CGro16NWGMCAC | Install automatic door closer on walk-in cooler doors | BCR | NW | Z16 | 0.127 | 827.39 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | N/A | Install automatic door closer on walk-in cooler doors | BCR | OTR | Z16 | 0.111 | 823.98 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | N/A | Install automatic door closer on walk-in cooler doors | BCR | 3 | OTR | 0.19 | 890.93 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | N/A | Install automatic door closer on walk-in cooler doors | BCR | 5 | OTR | 0.111 | 823.98 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | N/A | Install automatic door closer on walk-in cooler doors | BCR | 75 | OTR | 0.159 | 1007.88 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | N/A | Install automatic door closer on walk-in cooler doors | BCR | 85 | OTR | 0.127 | 1018.88 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | N/A | Install automatic door closer on walk-in cooler doors | BCR | 96 | OTR | 0.19 | 942.71 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | N/A | Install automatic door closer on walk-in cooler doors | BCR | NW | OTR | 0.127 | 827.39 | 0 | $0 | $120.00 | $156.82 | 8 |
| R79 | N/A | Install automatic door closer on walk-in cooler doors | BCR | OTR | OTR | 0.111 | 823.98 | 0 | $0 | $120.00 | $156.82 | 8 |

Units: Installed auto-closer (closer)

# At-A-Glance Measure List

| Measure Code | DEER RunID | Measure Description | Building Type | Building Vintage | Climate Zone | Peak Electric Demand Reduction (kW/ Closer) | Electric Savings (kWh/ Closer) | Gas Savings (therms/ Closer) | Base Case Cost | Measure Cost | Measure Incremental Cost | Effective Useful Life (years) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  | ($/Closer) | ($/Closer) | ($/Closer) |  |
| R80 | CGro0103GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 3 | Z01 | 0.111 | 2071.42 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0105GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 5 | Z01 | 0.111 | 2122.13 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0175GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 75 | Z01 | 0.333 | 2597.46 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0185GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 85 | Z01 | 0.37 | 2591.96 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0196GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 96 | Z01 | 0.185 | 2303.79 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro01NWGMFAC | Install automatic door closer on walk-in freezer doors | BCR | NW | Z01 | 0.111 | 2127.13 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | N/A | Install automatic door closer on walk-in freezer doors | BCR | OTR | Z01 | 0.111 | 2071.42 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0203GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 3 | Z02 | 0.407 | 2221.33 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0205GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 5 | Z02 | 0.407 | 2138.29 | 0 | $0.00 | $120.00 | $156.82 | 8 |

| R80 | CGro0275GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 75 | Z02 | 0.667 | 2789.13 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| R80 | CGro0285GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 85 | Z02 | 0.444 | 2790.58 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0296GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 96 | Z02 | 0.333 | 2311.92 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro02NWGMFAC | Install automatic door closer on walk-in freezer doors | BCR | NW | Z02 | 0.148 | 2119.46 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | N/A | Install automatic door closer on walk-in freezer doors | BCR | OTR | Z02 | 0.148 | 2119.46 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0303GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 3 | Z03 | 0.148 | 2090.25 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0305GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 5 | Z03 | 0.259 | 2029.33 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0375GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 75 | Z03 | 0.407 | 2813.63 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0385GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 85 | Z03 | 0.37 | 2764 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0396GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 96 | Z03 | 0.296 | 2273.96 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro03NWGMFAC | Install automatic door closer on walk-in freezer doors | BCR | NW | Z03 | 0.333 | 2034.08 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | N/A | Install automatic door closer on walk-in freezer doors | BCR | OTR | Z03 | 0.333 | 2034.08 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0403GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 3 | Z04 | 0.333 | 2037.25 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0405GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 5 | Z04 | 0.259 | 2072.67 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0475GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 75 | Z04 | 0.407 | 2773.42 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0485GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 85 | Z04 | 0.407 | 2736.75 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0496GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 96 | Z04 | 0.407 | 2203.46 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro04NWGMFAC | Install automatic door closer on walk-in freezer doors | BCR | NW | Z04 | 0.148 | 2088.75 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | N/A | Install automatic door closer on walk-in freezer doors | BCR | OTR | Z04 | 0.333 | 2037.25 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0503GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 3 | Z05 | 0.185 | 2070.83 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0505GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 5 | Z05 | 0.185 | 1985.42 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0575GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 75 | Z05 | 0.148 | 2804.46 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0585GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 85 | Z05 | 0.148 | 2710.46 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro0596GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 96 | Z05 | 0.296 | 2317.21 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro05NWGMFAC | Install automatic door closer on walk-in freezer doors | BCR | NW | Z05 | 0.185 | 1982.58 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | N/A | Install automatic door closer on walk-in freezer doors | BCR | OTR | Z05 | 0.185 | 1982.58 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1103GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 3 | Z11 | 0.296 | 2229.21 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1105GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 5 | Z11 | 0.296 | 2099.42 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1175GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 75 | Z11 | 0.519 | 2806.46 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1185GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 85 | Z11 | 0.519 | 2806.67 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1196GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 96 | Z11 | 0.185 | 2343.08 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro11NWGMFAC | Install automatic door closer on walk-in freezer doors | BCR | NW | Z11 | 0.259 | 2085.75 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | N/A | Install automatic door closer on walk-in freezer doors | BCR | OTR | Z11 | 0.259 | 2085.75 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1203GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 3 | Z12 | 0.444 | 2203.58 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1205GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 5 | Z12 | 0.222 | 2164.58 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1275GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 75 | Z12 | 0.556 | 2752.92 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1285GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 85 | Z12 | 0.593 | 2787.5 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1296GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 96 | Z12 | 0.185 | 2356.83 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro12NWGMFAC | Install automatic door closer on walk-in freezer doors | BCR | NW | Z12 | 0.407 | 2132.63 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | N/A | Install automatic door closer on walk-in freezer doors | BCR | OTR | Z12 | 0.407 | 2132.63 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1303GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 3 | Z13 | 0.333 | 2214.17 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1305GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 5 | Z13 | 0.37 | 2117.88 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1375GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 75 | Z13 | 0.556 | 2911.75 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1385GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 85 | Z13 | 0.815 | 2918.71 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1396GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 96 | Z13 | 0.296 | 2444.92 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro13NWGMFAC | Install automatic door closer on walk-in freezer doors | BCR | NW | Z13 | 0.185 | 2136.42 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | N/A | Install automatic door closer on walk-in freezer doors | BCR | OTR | Z13 | 0.37 | 2117.88 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1603GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 3 | Z16 | 0.148 | 2190.04 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1605GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 5 | Z16 | 0.333 | 2046.96 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1675GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 75 | Z16 | 0.37 | 2672 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1685GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 85 | Z16 | 0.37 | 2687.04 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro1696GMFAC | Install automatic door closer on walk-in freezer doors | BCR | 96 | Z16 | 0.407 | 2335.83 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | CGro16NWGMFAC | Install automatic door closer on walk-in freezer doors | BCR | NW | Z16 | 0.148 | 2043.04 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | N/A | Install automatic door closer on walk-in freezer doors | BCR | OTR | Z16 | 0.148 | 2043.04 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | N/A | Install automatic door closer on walk-in freezer doors | BCR | 3 | OTR | 0.333 | 2037.25 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | N/A | Install automatic door closer on walk-in freezer doors | BCR | 5 | OTR | 0.185 | 1985.42 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | N/A | Install automatic door closer on walk-in freezer doors | BCR | 75 | OTR | 0.333 | 2597.46 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | N/A | Install automatic door closer on walk-in freezer doors | BCR | 85 | OTR | 0.37 | 2591.96 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | N/A | Install automatic door closer on walk-in freezer doors | BCR | 96 | OTR | 0.407 | 2203.46 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | N/A | Install automatic door closer on walk-in freezer doors | BCR | NW | OTR | 0.185 | 1982.58 | 0 | $0.00 | $120.00 | $156.82 | 8 |
| R80 | N/A | Install automatic door closer on walk-in freezer doors | BCR | OTR | OTR | 0.185 | 1982.58 | 0 | $0.00 | $120.00 | $156.82 | 8 |

Units: Installed auto-closer (closer)

# Work Paper Approvals

| Charles Harmstead Supervisor, Energy Efficiency Engineering | Date |
| --- | --- |
| Peter Ford Manager, Energy Efficiency Engineering | Date |

# Document Revision History

Revision # 		Date 		         Description		         Author (Company)

| Revision 0 | 04/08/08 | Original workpaper: Auto-Closer Main Doors PGECOREF110 R0.doc | John Shen (KEMA Services Inc.) |
| --- | --- | --- | --- |
| Revision 1 | 05/28/09 | DEER 2008 update, minor edits | Breesa Kassing, PG&E Michele Friedrich, PG&E |
| Revision 1 | 11/09/09 | Added OTR to Climate Zone and Vintage Type in At-A-Glance table | Andrew Wieszczyk, PG&E |
| Revision 0 | 8/17/12 | Adopted from PGECOREF110 R1 Auto-Closers Main Doors.doc, updated November 9, 2009. Updated NTG values to DEER 2011 (August 28, 2012) | Kelvin Valenzuela, SDG&E |

# Table of Contents

At-A-Glance Summary	i

At-A-Glance Measure List	ii

At-A-Glance Measure List	vii

Work Paper Approvals	xii

Document Revision History	xiii

Table of Contents	xiv

Section 1. General Measure & Baseline Data	1

1.1 Measure Description & Background	1

Catalog Description	1

Program Restrictions and Guidelines	1

Technical Description	1

1.2 DEER Differences Analysis	1

1.3 Codes & Standards Requirements Analysis	1

1.4 EM&V, Market Potential, and Other Studies	2

1.5 Base Cases for Savings Estimates: Existing & Above Code	2

1.6 Base Cases & Measure Effective Useful Lives	2

1.7 Net-to-Gross Ratios for Different Program Strategies	2

Section 2. Calculation Methods	2

2.1 Electric Energy Savings Estimation Methodologies	2

2.2 Demand Reduction Estimation Methodologies	2

2.3 Gas Energy Savings Estimation Methodologies	2

Section 3. Load Shapes	2

3.1 Base Case Load Shapes	3

3.2 Measure Load Shapes	3

Section 4. Base Case & Measure Costs	3

4.1 Base Case Costs	3

4.2 Measure Costs	3

4.3 Incremental & Full Measure Costs	3

References	5

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

### Catalog Description

The auto-closer should be applied to the main insulated opaque door(s) of a walk-in cooler or freezer. The auto-closer must be able to firmly close that door when it is within one inch of full closure.

### Program Restrictions and Guidelines

This measure applies to the installation of door closers on either main cooler or main freezer doors.  Customer must be a current PG&E customer to be eligible for rebates.

### Technical Description

Cooler and freezer doors that are left open increase air infiltration into the refrigerated space which in turn leads to a higher cooling load.  Auto closers significantly reduce the infiltration of air into the refrigerated space.  Energy savings occur because the compressor will operate less frequently due to the reduction in load in a properly closed cooler or freezer.

This measure provides auto-closers for walk-in coolers and freezers that will close the doors automatically when the door is within one inch of full closure.

## 1.2 DEER Differences Analysis

Energy savings and cost data are based on DEER data for Measure IDs D03-208 and D03-209.  Section 7.3, Grocery Refrigeration Measures, of the DEER Report, directly provides savings and cost data for auto-closers, however a few assumptions had to be made to comply with the rebate structure.  DEER offers savings and cost data per cooler or freezer where as rebates are paid per closer.  This workpaper assumes that there is an average of one auto-closer or one door per cooler or freezer.

DEER offers data for auto-closers only for the grocery sector.  These measures are applicable for all building types with walk-in coolers and freezers and savings are comparable to the grocery store savings.

DEER also gives negative gas savings which would only be true if the refrigeration system condenser was rejecting heat into the conditioned space.  However, this measure is for walk-in doors which typically have condensers that reject heat outside, so there is no interaction with the HVAC system and the condenser.  There are interactive effects with the HVAC system through reduced infiltration which would have positive heating (gas) savings and negative cooling (electric) savings but we will not address them until the next revision of this workpaper.

## 1.3 Codes & Standards Requirements Analysis

The California Energy Commission's (CEC) Title 20 Appliance Standards require automatic door closers for all walk-in coolers and freezers manufactured on or after January 1, 2006.  There are, however, no code requirements for auto closers for units before this date.  Code baseline used in DEER assumes no auto-closers.

## 1.4 EM&V, Market Potential, and Other Studies

There were no specific EM&V studies identified that addressed the auto-closer measures.

## 1.5 Base Cases for Savings Estimates: Existing & Above Code

Above-code and existing base cases in DEER assume that there are no auto-closers installed on cooler or freezer doors.

## 1.6 Base Cases & Measure Effective Useful Lives

The measure effective useful life for auto door closers is 8 years based on 2008 DEER EUL/RUL Values and Summary Documentation (Updated 10 October 2008).

## 1.7 Net-to-Gross Ratios for Different Program Strategies

DEER 2011 recommend a net-to-gross ratio (NTGR) of 0.60 for all energy efficiency measures (EEMs) covered under this program4.  The referenced NTGR table suggest the 0.60 Value for NTGR for the category labeled “All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years”.  Demand ventilation controls fall into this category.

# Section 2. Calculation Methods

## 2.1 Electric Energy Savings Estimation Methodologies

Energy savings in DEER are based on an assumed percentage decrease in infiltration for coolers or freezers when an auto-closer is installed.  A decrease in infiltration decreases the cooling load and thus results in energy savings.  Savings are based on an assumed infiltration decrease of 40%.  Actual savings depend on vintage, climate zone and application (cooler and freezer).

## 2.2 Demand Reduction Estimation Methodologies

Savings are based on decreased infiltration when compared to the base case refrigeration without auto-closers as stated in 2004-2005 DEER (D03-208, D03-209) section 7.  Actual savings depend on vintage, climate zone and application (cooler and freezer.)Error: Reference source not found

## 2.3 Gas Energy Savings Estimation Methodologies

There are no gas energy savings for this measure.

# Section 3. Load Shapes

Load Shapes are an important part of the life-cycle cost analysis of any energy efficiency program portfolio.  The net benefits associated with a measure are based on the amount of energy saved and the avoided cost per unit of energy saved.  For electricity, the avoided cost varies hourly over an entire year.  Thus, the net benefits calculation for a measure requires both the total annual energy savings (kWh) of the measure and the distribution of that savings over the year.  The distribution of savings over the year is represented by the measure’s load shape.  The measure’s load shape indicates what fraction of annual energy savings occurs in each time period of the year.  An hourly load shape indicates what fraction of annual savings occurs for each hour of the year.  A Time-of-Use (TOU) load shape indicates what fraction occurs within five or six broad time-of-use periods, typically defined by a specific utility rate tariff.  Formally, a load shape is a set of fractions summing to unity, one fraction for each hour or for each TOU period.  Multiplying the measure load shape with the hourly avoided cost stream determines the average avoided cost per kWh for use in the life cycle cost analysis that determines a measure’s Total Resource Cost (TRC) benefit.

## 3.1 Base Case Load Shapes

The base case load shape is expected to follow a typical non-residential refrigeration end use load shape

## 3.2 Measure Load Shapes

For purposes of the net benefits estimates in the E3 calculator, what is required is the load shape that ideally represents the difference between the base equipment and the installed energy efficiency measure.  This difference load profile is what is called the Measure Load Shape and would be the preferred load shape for use in the net benefits calculations.

The E3 Calculator contains a fixed set of load shapes selections that are the combination of the hourly avoided costs and the load shape data that was available at the time of the tool’s creation. The most common occupancy types for this measure include Grocery and Restaurants.  In the E3 Calculator, the Measure Electric End Use Shape for refrigeration is the best representation of the measure load shape for both occupancy types.

# Section 4. Base Case & Measure Costs

The DEER Measure Cost Data Users Guide, version 2.01, defines the following terms:

- Retrofit (RET) – replacing a working technology prior to failure.

- Replace on Burnout (ROB) – replacing a technology at the end of its useful life.

- New Construction (NEW) – installing a technology in a new construction or major renovation project.

Auto closers are suitable for RET or NEW.

## 4.1 Base Case Costs

The base case for these measures is a cooler without auto-closer installed on door; therefore the base case cost is $0.

## 4.2 Measure Costs

DEER 2008 provides material cost data for this measure as $120 per auto-closer installed.5

## 4.3 Incremental & Full Measure Costs

DEER 2008 lists this measure application as either a retrofit (RET) or new construction (NEW) and so the cost is the full installed cost.Error: Reference source not found

DEER 2008 provides cost data on labor as $36. 82 and equipment cost as $120, the sum of which is the full cost of the measure, $156.82/closer.

Index

California Energy Commission	1

DEER	1, 2, 3, 5

DEER Measure Cost Data Users Guide	3

E3 calculator	3

New Construction	3

Replace on Burnout	3

Retrofit	3

Title 20	1

# References

2004-2005 Database for Energy Efficiency Resources (DEER) Update Study, prepared by Itron Inc., December 2005, Section 7-76, Section 7-77.

California Code of Regulations, Title 20, pp 225, February 2008

2008 DEER EUL/RUL Values and Summary Documentation (Updated 10 October 2008).

54DEER 2011 Net-To-Gross Ratios.  (“DEER2011-NTG_IncludingCarryoversFromDEER2008_2011-12-07.xls”, accessed March 26, 2012 at http://www.deeresources.com/index).