## Res Serv Costs
San Diego Gas and Electric
Electric Marginal Customer Cost Development
Residential Service Costs by Load Size and Voltage level
120/240 Single Phase
Line No. | Max Annual Demand (kW) | Service Length | Wire Type* |  | No. of Runs | Cost Per Foot** | Total Cost Installed ***
| (a) | (b) | (c) |  | (d) | (e) | (f)
1 | 0 - 2 | 25 | #2 (1ph) |  | 1 | 2.2724 | 138.713
2 | 3 - 6 | 25 | #2 (1ph) |  | 1 | 2.2724 | 138.713
3 | 7 - 12 | 50 | #2 (1ph) |  | 1 | 2.2724 | 195.5223
4 | 13 - 20 | 50 | 1/0 (1ph) |  | 1 | 2.6366 | 213.7318
5 | 21 - 25 | 50 | 1/0 (1ph) |  | 1 | 2.6366 | 213.7318
6 | 26 - 50 | 100 | 3/0 (1ph) |  | 1 | 4.3337 | 515.2782
7 | 51 - 75 | 100 | 350 (1ph) |  | 1 | 7.4827 | 830.1737
8 | 76 - 100 | 100 | 350 (1ph) |  | 2 | 7.4827 | 1578.4436
9 | 101 - 150 | 100 | 350 (1ph) |  | 3 | 7.4827 | 2326.7136
10 | 151 - 200 | 100 | 350 (1ph) |  | 3 | 7.4827 | 2326.7136
11 | 201 - 250
12 | 251 - 350
13 | 351 - 450
14 | 451 - 500
15 | 501 - 550
16 | 551 - 650
17 | 651 - 750
18 | 751 - 850
19 | 851 - 1,050
20 | 1,051 - 1,250
21 | 1,251 - 1,500
22 | 1,501 - 2,000
23 | 2,001 - 2,500
24 | 2,501 - 3,000
25 | 3,001 - 3,500
26 | 3,501 - 4,000
27 | 4,001 - 5,000
28 | 5,001 - 12,000
29 | 12,001 - 25,000
30 | 25,001 - 50,000
31 | >50,000
Notes:
- Col. (f) = [Col. (b) *Col. (d) * Col. (e)]
* Based on SDG&E Electric Distribution Design Manual & Standards
** Based on fully loaded 2017 DPSS costs
*** Total Costs also include Slip-Fit Connector installed cost.

## CI Serv Costs
San Diego Gas and Electric
Electric Marginal Customer Cost Development
C/I Service Costs by Load Size and Voltage level
|  |  |  | 120/240 | [5 empty] | 120/208 |  |  |  | 277/480 |  |  |  |  | 12 kV Primary
Line No. | Max Annual Demand (kW) | Service Length | Wire Type* |  | No. of Runs | Cost Per Foot** | Total Cost Installed | Service Length | Wire Type* |  | No. of Runs | Cost Per Foot** | Total Cost Installed | Service Length | Wire Type* | No. of Runs | Cost Per Foot** | Total Cost Installed | Service Length | Wire Type* | No. of Runs | Cost Per Foot** | Total Cost Installed
| (a) | (b) | (c) |  | (d) | (e) | (f) | (g) | (h) |  | (i) | (j) | (k) | (l) | (m) | (n) | (o) | (p) | (l) | (m) | (n) | (o) | (p)
1 | 0 - 2 | 25 | 3/0 (3ph) |  | 1 | 5.3657 | 754.1427 | 25 | 3/0 (3ph) |  | 1 | 5.3657 | 754.1427 | 25 | 3/0 (3ph) | 1 | 5.3657 | 754.1427 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
2 | 3 - 6 | 25 | 3/0 (3ph) |  | 1 | 5.3657 | 754.1427 | 25 | 3/0 (3ph) |  | 1 | 5.3657 | 754.1427 | 25 | 3/0 (3ph) | 1 | 5.3657 | 754.1427 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
3 | 7 - 12 | 50 | 3/0 (3ph) |  | 1 | 5.3657 | 888.2856 | 50 | 3/0 (3ph) |  | 1 | 5.3657 | 888.2856 | 50 | 3/0 (3ph) | 1 | 5.3657 | 888.2856 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
4 | 13 - 20 | 50 | 3/0 (3ph) |  | 1 | 5.3657 | 888.2856 | 50 | 3/0 (3ph) |  | 1 | 5.3657 | 888.2856 | 50 | 3/0 (3ph) | 1 | 5.3657 | 888.2856 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
5 | 21 - 25 | 50 | 3/0 (3ph) |  | 1 | 5.3657 | 888.2856 | 50 | 3/0 (3ph) |  | 1 | 5.3657 | 888.2856 | 50 | 3/0 (3ph) | 1 | 5.3657 | 888.2856 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
6 | 26 - 50 | 100 | 3/0 (3ph) |  | 1 | 5.3657 | 1156.5714 | 100 | 3/0 (3ph) |  | 1 | 5.3657 | 1156.5714 | 100 | 3/0 (3ph) | 1 | 5.3657 | 1156.5714 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
7 | 51 - 75 | 100 | 350 (3ph) |  | 1 | 9.2836 | 1781.476 | 100 | 350 (3ph) |  | 1 | 9.2836 | 1781.476 | 100 | 3/0 (3ph) | 1 | 5.3657 | 1156.5714 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
8 | 76 - 100 | 100 | 350 (3ph) |  | 1 | 9.2836 | 1781.476 | 100 | 350 (3ph) |  | 1 | 9.2836 | 1781.476 | 100 | 350 (3ph) | 1 | 9.2836 | 1781.476 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
9 | 101 - 150 | 100 | 350 (3ph) |  | 2 | 9.2836 | 3562.952 | 100 | 350 (3ph) |  | 2 | 9.2836 | 3562.952 | 100 | 350 (3ph) | 1 | 9.2836 | 1781.476 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
10 | 151 - 200 | 100 | 500 (3ph) |  | 2 | 14.6914 | 4799.963 | 100 | 500 (3ph) |  | 2 | 14.6914 | 4799.963 | 100 | 500 (3ph) | 1 | 14.6914 | 2399.9815 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
11 | 201 - 250 | 100 | 500 (3ph) |  | 2 | 14.6914 | 4799.963 | 100 | 500 (3ph) |  | 2 | 14.6914 | 4799.963 | 100 | 500 (3ph) | 1 | 14.6914 | 2399.9815 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
12 | 251 - 350 | 100 | 1000 (3ph) |  | 2 | 26.7414 | 7831.0277 | 100 | 1000 (3ph) |  | 2 | 26.7414 | 7831.0277 | 100 | 1000 (3ph) | 1 | 26.7414 | 3915.5138 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
13 | 351 - 450 | 100 | 1000 (3ph) |  | 3 | 26.7414 | 11746.5415 | 100 | 1000 (3ph) |  | 3 | 26.7414 | 11746.5415 | 100 | 500 (3ph) | 2 | 14.6914 | 4799.963 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
14 | 451 - 500 | 100 | 1000 (3ph) |  | 3 | 26.7414 | 11746.5415 | 100 | 1000 (3ph) |  | 3 | 26.7414 | 11746.5415 | 100 | 500 (3ph) | 2 | 14.6914 | 4799.963 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
15 | 501 - 550 | 100 | 1000 (3ph) |  | 3 | 26.7414 | 11746.5415 | 100 | 1000 (3ph) |  | 3 | 26.7414 | 11746.5415 | 100 | 500 (3ph) | 2 | 14.6914 | 4799.963 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
16 | 551 - 650 | 100 | 1000 (3ph) |  | 4 | 26.7414 | 15662.0554 | 100 | 1000 (3ph) |  | 4 | 26.7414 | 15662.0554 | 100 | 1000 (3ph) | 2 | 26.7414 | 7831.0277 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
17 | 651 - 750 | 100 | 1000 (3ph) |  | 5 | 26.7414 | 19577.5692 | 100 | 1000 (3ph) |  | 5 | 26.7414 | 19577.5692 | 100 | 1000 (3ph) | 2 | 26.7414 | 7831.0277 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
18 | 751 - 850 | 100 | 1000 (3ph) |  | 6 | 26.7414 | 23493.0831 | 100 | 1000 (3ph) |  | 6 | 26.7414 | 23493.0831 | 100 | 1000 (3ph) | 2 | 26.7414 | 7831.0277 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
19 | 851 - 1,050 | 100 | 1000 (3ph) |  | 9 | 26.7414 | 35239.6246 | 100 | 1000 (3ph) |  | 9 | 26.7414 | 35239.6246 | 100 | 1000 (3ph) | 3 | 26.7414 | 11746.5415 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
20 | 1,051 - 1,250 | 100 | 1000 (3ph) |  | 12 | 26.7414 | 46986.1662 | 100 | 1000 (3ph) |  | 12 | 26.7414 | 46986.1662 | 100 | 1000 (3ph) | 4 | 26.7414 | 15662.0554 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
21 | 1,251 - 1,500 | 100 | 1000 (3ph) |  | 12 | 26.7414 | 46986.1662 | 100 | 1000 (3ph) |  | 12 | 26.7414 | 46986.1662 | 100 | 1000 (3ph) | 5 | 26.7414 | 19577.5692 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
22 | 1,501 - 2,000 | 100 | 1000 (3ph) |  | 12 | 26.7414 | 46986.1662 | 100 | 1000 (3ph) |  | 12 | 26.7414 | 46986.1662 | 100 | 1000 (3ph) | 8 | 26.7414 | 31324.1108 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
23 | 2,001 - 2,500 | [12 empty] | 100 | 1000 (3ph) | 10 | 26.7414 | 39155.1385 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
24 | 2,501 - 3,000 | [12 empty] | 100 | 1000 (3ph) | 12 | 26.7414 | 46986.1662 | 100 | 2/0 (3ph) | 1 | 21.972 | 3870.6679
25 | 3,001 - 3,500 | [12 empty] | 100 | 1000 (3ph) | 12 | 26.7414 | 46986.1662 | 100 | 1000 (3ph) | 1 | 64.8722 | 9612.4995
26 | 3,501 - 4,000 | [12 empty] | 100 | 1000 (3ph) | 12 | 26.7414 | 46986.1662 | 100 | 1000 (3ph) | 1 | 64.8722 | 9612.4995
27 | 4,001 - 5,000 | [12 empty] | 100 | 1000 (3ph) | 12 | 26.7414 | 46986.1662 | 100 | 1000 (3ph) | 1 | 64.8722 | 9612.4995
28 | 5,001 - 12,000 | [12 empty] | 100 | 1000 (3ph) | 12 | 26.7414 | 46986.1662 | 100 | 1000 (3ph) | 1 | 64.8722 | 9612.4995
29 | 12,001 - 25,000 | [17 empty] | 100 | 1000 (3ph) | 1 | 64.8722 | 9612.4995
30 | 25,001 - 50,000 | [17 empty] | 100 | 1000 (3ph) | 1 | 64.8722 | 9612.4995
31 | >50,000 | [17 empty] | 100 | 1000 (3ph) | 1 | 64.8722 | 9612.4995
[19 empty] | Transmission Service Costs: | 1221.2319
- Col. (f) = [(Col. (b) *Col. (d) * Col. (e)) + (Compression Lugs * Col. (d)]
| - Col. (k) = [(Col. (g) *Col. (i) * Col. (j)) + (Compression Lugs * Col. (i)] | [17 empty] | Transmission Cost Factor | 18.8252
- Col. (f) = [(Col. (b) *Col. (d) * Col. (e)) + (Compression Lugs * Col. (d)]
* Based on SDG&E Electric Distribution Design Manual & Standards
** Based on fully loaded 2017 DPSS costs

## Compression Lugs_Wire
Sec/Srvc Wire Type | DPSS Cost per Foot* | Compression Lugs | DPSS Cost*
#2 (1ph) | 2.2724
1/0 (1ph) | 2.6366 | 1- 2 Hole Lug (#2-3/0) | 154.9719
3/0 (1ph) | 4.3337 | 1- 2 Hole Lug (350-500) | 232.6544
350 (1ph) | 7.4827 | 1- 2 Hole Lug (1000) | 310.0524
3/0 (3ph) | 5.3657 | 1- Slip Fit (350-8S, 350-8L) #8-350 and CONN-S | 11.6808
350 (3ph) | 9.2836 | 1- Slip Fit (500-8S) #6-500 and CONN-S | 48.5609
500 (3ph) | 14.6914
750 (3ph) | NA | 2-Hole Lugs (3-1000 & 1-750) | 1241.3695
1000 (3ph) | 26.7414 | 2-Hole Lugs (3-500 & 1-350) | 930.8372
|  | 2-Hole Lugs (3-350 & 1-3/0) | 853.111
Slip Fit 8W with Labor | 81.9038 | 2-Hole Lugs (3-3/0 &1-1/0) | 619.9998
Primary Cable | DPSS Cost per Foot** | Primary Connections SDG&E Source | DPSS Cost **
PJN2/0 | 21.972 | LBE2/0 | 201.3339
PJ1000 | 64.8722 | AD1MIL | 22.5502
|  | ELBO-T | 476.6396
|  | PLUG-F | 64.9251
|  | SP1000 | 34.7946
|  | Total for PJ1000 | 598.9095
`
Notes:
* Based on fully loaded DPSS costs provided by Project Management 04-13-17
** Primary Cable and Connections costs based on fully loaded DPSS costs provided
by Project Management 04-13-17
|  | Primary Connections @ Primary Meter | DPSS Cost **
|  | SC-2/0 | 356.4901
|  | Total 2/0 per phase cost | 356.4901
|  | SC1000 | 442.8489
|  | Total 1000 KCMIL | 442.8489

## Avg TXFMR Costs
San Diego Gas and Electric
Electric Marginal Customer Cost Development
Residential Transformer Costs by Load Size and Voltage level
|  | 120/240 Single Phase |  |  |  |  | 120/240 - Three Phase |  |  |  | 120/208 |  |  |  | 277/480
Line No. | Max Annual Demand (KW) | Transformer Size | Transformer Cost |  | Avg. Cust. Per Txfmr | Avg. Txfmr Cost | Transformer Size | Transformer Cost | Avg. Cust. Per Txfmr | Avg. Txfmr Cost | Transformer Size | Transformer Cost | Avg. Cust. Per Txfmr | Avg. Txfmr Cost | Transformer Size | Transformer Cost | Avg. Cust. Per Txfmr | Avg. Txfmr Cost
| (a) | (b) | ('c) |  | (d) | (e) | (f) | (g) | (h) | (i)
1 | 0 - 2 | 25 | 5398.6031 |  | 22 | 245.391 | 75 | 17458.8866 | 60 | 290.9814 | 75 | 18357.4023 | 60 | 305.9567 | 150 | 21654.459 | 60 | 360.9076
2 | 3 - 6 | 25 | 5398.6031 |  | 7 | 771.229 | 75 | 17458.8866 | 20 | 872.9443 | 75 | 18357.4023 | 20 | 917.8701 | 150 | 21654.459 | 20 | 1082.7229
3 | 7 - 12 | 25 | 5398.6031 |  | 8 | 674.8254 | 75 | 17458.8866 | 10 | 1745.8887 | 75 | 18357.4023 | 10 | 1835.7402 | 150 | 21654.459 | 10 | 2165.4459
4 | 13 - 20 | 25 | 5398.6031 |  | 4 | 1349.6508 | 75 | 17458.8866 | 4 | 4364.7216 | 75 | 18357.4023 | 4 | 4589.3506 | 150 | 21654.459 | 4 | 5413.6147
5 | 21 - 25 | 25 | 5398.6031 |  | 4 | 1349.6508 | 75 | 17458.8866 | 4 | 4364.7216 | 75 | 18357.4023 | 4 | 4589.3506 | 150 | 21654.459 | 4 | 5413.6147
6 | 26 - 50 | 50 | 5800.069 |  | 4 | 1450.0173 | 75 | 17458.8866 | 2 | 8729.4433 | 75 | 18357.4023 | 2 | 9178.7012 | 150 | 21654.459 | 3 | 7218.153
7 | 51 - 75 | 75 | 6368.9187 |  | 2 | 3184.4593 | 75 | 17458.8866 | 1 | 17458.8866 | 75 | 18357.4023 | 1 | 18357.4023 | 150 | 21654.459 | 2 | 10827.2295
8 | 76 - 100 | 100 | 6104.428 |  | 2 | 3052.214 | 225 | 20625.5576 | 2 | 10312.7788 | 150 | 21264.5312 | 2 | 10632.2656 | 150 | 21654.459 | 2 | 10827.2295
9 | 101 - 150 | 100 | 6104.428 |  | 1 | 6104.428 | 225 | 20625.5576 | 2 | 10312.7788 | 150 | 21264.5312 | 1 | 21264.5312 | 150 | 21654.459 | 1 | 21654.459
10 | 151 - 200 | 167 | 8622.4294 |  | 1 | 8622.4294 | 225 | 20625.5576 | 1 | 20625.5576 | 300 | 23960.5311 | 2 | 11980.2656 | 300 | 22684.1377 | 2 | 11342.0688
11 | 201 - 250 | [5 empty] | 225 | 20625.5576 | 1 | 20625.5576 | 300 | 23960.5311 | 2 | 11980.2656 | 300 | 22684.1377 | 2 | 11342.0688
12 | 251 - 350 | [9 empty] | 300 | 23960.5311 | 1 | 23960.5311 | 300 | 22684.1377 | 1 | 22684.1377
13 | 351 - 450 | [9 empty] | 500 | 30684.9708 | 1 | 30684.9708 | 300 | 22684.1377 | 1 | 22684.1377
14 | 451 - 500 | [9 empty] | 750 | 41473.2999 | 2 | 20736.65 | 750 | 35043.2369 | 2 | 17521.6184
15 | 501 - 550 | [9 empty] | 750 | 41473.2999 | 2 | 20736.65 | 750 | 35043.2369 | 2 | 17521.6184
16 | 551 - 650 | [9 empty] | 750 | 41473.2999 | 2 | 20736.65 | 750 | 35043.2369 | 2 | 17521.6184
17 | 651 - 750 | [9 empty] | 1000 | 48693.2734 | 2 | 24346.6367 | 1000 | 42483.1317 | 2 | 21241.5658
18 | 751 - 850 | [9 empty] | 1000 | 48693.2734 | 1 | 48693.2734 | 1000 | 42483.1317 | 1 | 42483.1317
19 | 851 - 1,050 | [9 empty] | 1000 | 48693.2734 | 1 | 48693.2734 | 1500 | 49082.6982 | 2 | 24541.3491
20 | 1,051 - 1,250 | [9 empty] | 1000 | 48693.2734 | 1 | 48693.2734 | 1500 | 49082.6982 | 1 | 49082.6982
21 | 1,251 - 1,500 | [9 empty] | 1000 | 48693.2734 | 1 | 48693.2734 | 1500 | 49082.6982 | 1 | 49082.6982
22 | 1,501 - 2,000 | [9 empty] | 1000 | 48693.2734 | 1 | 48693.2734 | 2000 | 62400.8929 | 1 | 62400.8929
23 | 2,001 - 2,500 | [13 empty] | 2000 | 62400.8929 | 1 | 62400.8929
24 | 2,501 - 3,000 | [13 empty] | 2500 | 68150.5678 | 1 | 68150.5678
25 | 3,001 - 3,500
26 | 3,501 - 4,000
27 | 4,001 - 5,000
28 | 5,001 - 12,000
29 | 12,001 - 25,000
30 | 25,001 - 50,000
31 | >50,000
Notes:
- Transformer costs assume one customer per transformer for loads > 25KW
- 120/240 Three Phase transformer costs are based on 120/208 transformer costs
- Transformer costs reflect 2016 costs escalated to 2017 dollars. |  |  |  | 2017 Escalation Factor:
San Diego Gas and Electric
Electric Marginal Customer Cost Development
C/I Transformer Costs by Load Size and Voltage level
|  | 120/240 Single Phase |  |  |  |  | 120/240 - Three Phase |  |  |  | 120/208 |  |  |  | 277/480
Line No. | Max Annual Demand | Transformer Size | Transformer Cost |  | Avg. Cust. Per Txfmr | Avg. Txfmr Cost | Transformer Size | Transformer Cost | Avg. Cust. Per Txfmr | Avg. Txfmr Cost | Transformer Size | Transformer Cost | Avg. Cust. Per Txfmr | Avg. Txfmr Cost | Transformer Size | Transformer Cost | Avg. Cust. Per Txfmr | Avg. Txfmr Cost
| (a) | (b) | ('c) |  | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k) | (l) | (m) | (n) | (o) | (p) | (q)
1 | 0 - 2 | 25 | 5398.6031 |  | 15 | 359.9069 | 75 | 17458.8866 | 42 | 415.6878 | 75 | 18357.4023 | 42 | 437.081 | 150 | 21654.459 | 42 | 515.5824
2 | 3 - 6 | 25 | 5398.6031 |  | 5 | 1079.7206 | 75 | 17458.8866 | 14 | 1247.0633 | 75 | 18357.4023 | 14 | 1311.243 | 150 | 21654.459 | 14 | 1546.7471
3 | 7 - 12 | 50 | 5398.6031 |  | 5 | 1079.7206 | 75 | 17458.8866 | 7 | 2494.1267 | 75 | 18357.4023 | 7 | 2622.486 | 150 | 21654.459 | 7 | 3093.4941
4 | 13 - 20 | 50 | 5398.6031 |  | 2 | 2699.3015 | 75 | 17458.8866 | 3 | 5819.6289 | 75 | 18357.4023 | 3 | 6119.1341 | 150 | 21654.459 | 3 | 7218.153
5 | 21 - 25 | 50 | 5398.6031 |  | 2 | 2699.3015 | 75 | 17458.8866 | 3 | 5819.6289 | 75 | 18357.4023 | 3 | 6119.1341 | 150 | 21654.459 | 3 | 7218.153
6 | 26 - 50 | 50 | 5800.069 |  | 1 | 5800.069 | 75 | 17458.8866 | 1 | 17458.8866 | 75 | 18357.4023 | 1 | 18357.4023 | 150 | 21654.459 | 3 | 7218.153
7 | 51 - 75 | 75 | 6368.9187 |  | 1 | 6368.9187 | 75 | 17458.8866 | 1 | 17458.8866 | 75 | 18357.4023 | 1 | 18357.4023 | 150 | 21654.459 | 2 | 10827.2295
8 | 76 - 100 | 100 | 6104.428 |  | 1 | 6104.428 | 225 | 20625.5576 | 2 | 10312.7788 | 150 | 21264.5312 | 2 | 10632.2656 | 150 | 21654.459 | 2 | 10827.2295
9 | 101 - 150 | 100 | 6104.428 |  | 1 | 6104.428 | 225 | 20625.5576 | 2 | 10312.7788 | 150 | 21264.5312 | 1 | 21264.5312 | 150 | 21654.459 | 1 | 21654.459
10 | 151 - 200 | 167 | 8622.4294 |  | 1 | 8622.4294 | 225 | 20625.5576 | 1 | 20625.5576 | 300 | 23960.5311 | 2 | 11980.2656 | 300 | 22684.1377 | 2 | 11342.0688
11 | 201 - 250 | [5 empty] | 225 | 20625.5576 | 1 | 20625.5576 | 300 | 23960.5311 | 2 | 11980.2656 | 300 | 22684.1377 | 2 | 11342.0688
12 | 251 - 350 | [9 empty] | 300 | 23960.5311 | 1 | 23960.5311 | 300 | 22684.1377 | 1 | 22684.1377
13 | 351 - 450 | [9 empty] | 500 | 30684.9708 | 2 | 15342.4854 | 500 | 30684.9708 | 2 | 15342.4854
14 | 451 - 500 | [9 empty] | 750 | 41473.2999 | 2 | 20736.65 | 750 | 35043.2369 | 2 | 17521.6184
15 | 501 - 550 | [9 empty] | 750 | 41473.2999 | 2 | 20736.65 | 750 | 35043.2369 | 2 | 17521.6184
16 | 551 - 650 | [9 empty] | 750 | 41473.2999 | 1 | 41473.2999 | 750 | 35043.2369 | 1 | 35043.2369
17 | 651 - 750 | [9 empty] | 750 | 41473.2999 | 1 | 41473.2999 | 1000 | 42483.1317 | 1 | 42483.1317
18 | 751 - 850 | [9 empty] | 1000 | 48693.2734 | 1 | 48693.2734 | 1000 | 42483.1317 | 1 | 42483.1317
19 | 851 - 1,050 | [9 empty] | 1000 | 48693.2734 | 1 | 48693.2734 | 1500 | 49082.6982 | 1 | 49082.6982
20 | 1,051 - 1,250 | [9 empty] | 1000 | 48693.2734 | 1 | 48693.2734 | 1500 | 49082.6982 | 1 | 49082.6982
21 | 1,251 - 1,500 | [9 empty] | 1000 | 48693.2734 | 1 | 48693.2734 | 1500 | 49082.6982 | 1 | 49082.6982
22 | 1,501 - 2,000 | [9 empty] | 1000 | 48693.2734 | 1 | 48693.2734 | 2000 | 62400.8929 | 1 | 62400.8929
23 | 2,001 - 2,500 | [13 empty] | 2500 | 68150.5678 | 1 | 68150.5678
24 | 2,501 - 3,000 | [13 empty] | 2500 | 68150.5678 | 1 | 68150.5678
25 | 3,001 - 3,500 | [13 empty] | 2500 | 68150.5678 | 1 | 68150.5678
26 | 3,501 - 4,000 | [13 empty] | 2500 | 68150.5678 | 1 | 68150.5678
27 | 4,001 - 5,000 | [13 empty] | 2500 | 68150.5678 | 1 | 68150.5678
28 | 5,001 - 10,000 | [13 empty] | 2500 | 68150.5678 | 1 | 68150.5678
29 | 10,001 - 25,000
30 | 25,001 - 50,000
31 | >50,000
Notes:
- Transformer Costs reflect 2016 costs escalated to 2017 dollars.

## Avg. Meter Costs
San Diego Gas and Electric
Electric Marginal Customer Cost Development
Meter Costs by Load Size and Voltage level
|  | Residential |  |  | Commercial |  |  | Industrial
|  | Secondary | Secondary |  | Secondary | Secondary |  | Secondary
|  | 1-Phase | 3-Phase | Primary | 1-Phase | 3-Phase | Primary | 3-Phase | Primary
Line No. | Max Annual Demand (KW) | Total Meter Costs | Total Meter Costs | Total Meter Costs | Total Meter Costs | Total Meter Costs | Total Meter Costs | Total Meter Costs | Total Meter Costs
(a)
1 | 0 - 2 | 246.2433 | 373.18 | 1013.04 | 289.75 | 373.18 | 1070.55 | 1070.55 | 1196.87
2 | 3 - 6 | 246.2433 | 373.18 | 1013.04 | 289.75 | 373.18 | 1070.55 | 1070.55 | 1196.87
3 | 7 - 12 | 246.2433 | 373.18 | 1013.04 | 289.75 | 373.18 | 1070.55 | 1070.55 | 1196.87
4 | 13 - 20 | 246.2433 | 373.18 | 1013.04 | 289.75 | 373.18 | 1070.55 | 1070.55 | 1196.87
5 | 21 - 25 | 246.2433 | 373.18 | 1013.04 | 289.75 | 373.18 | 1070.55 | 1070.55 | 1196.87
6 | 26 - 50 | 246.2433 | 373.18 | 1013.04 | 289.75 | 373.18 | 1070.55 | 1070.55 | 1196.87
7 | 51 - 75 | 246.2433 | 373.18 | 1013.04 | 289.75 | 373.18 | 1070.55 | 1070.55 | 1196.87
8 | 76 - 100 | 246.2433 | 373.18 | 1013.04 | 289.75 | 373.18 | 1070.55 | 1070.55 | 1196.87
9 | 101 - 150 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
10 | 151 - 200 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
11 | 201 - 250 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
12 | 251 - 350 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
13 | 351 - 450 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
14 | 451 - 500 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
15 | 501 - 550 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
16 | 551 - 650 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
17 | 651 - 750 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
18 | 751 - 850 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
19 | 851 - 1,050 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
20 | 1,051 - 1,250 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
21 | 1,251 - 1,500 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
22 | 1,501 - 2,000 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
23 | 2,001 - 2,500 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
24 | 2,501 - 3,000 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
25 | 3,001 - 3,500 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
26 | 3,501 - 4,000 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
27 | 4,001 - 5,000 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
28 | 5,001 - 12,000 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
29 | 12,001 - 25,000 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
30 | 25,001 - 50,000 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87
31 | >50,000 | 246.2433 | 373.18 | 1013.04 | 289.75 | 1070.55 | 1196.87 | 1070.55 | 1196.87