## WMP_Table
ID of Circuit | County | Dates of Outages | # of Customers Affected | Measure taken, or planned to be taken, to reduce the need for, and impact of, future PSPS of circuit
1030 | San Diego | Oct 10-11, 2019 | 30 | • 26.4 miles of undergrounding completed to date; 28 miles in scope for 2022 • 2.3 miles of overhead hardening completed to date • Added or replaced 3 SCADA sectionalizing devices • 185 customers have benefitted from backup resiliency programs
|  | Oct 24-25, 2019 | 185
|  | Oct 30-31, 2019 | 1341
|  | Sept 9, 2020 | 30
|  | Dec 2-4, 2020 | 1182
|  | Dec 7-9, 2020 | 1363
|  | Dec 23-24, 2020 | 30
1166 | San Diego | Dec 2-4, 2020 | 322 | • 0.29 miles of overhead hardening completed to date • Added or replaced 1 SCADA sectionalizing device • 17 customers have benefitted from backup resiliency programs
|  | Dec 7-8, 2020 | 60
|  | Dec 23-24, 2020 | 322
1215 | San Diego | Oct 27, 2020 | 133 | • 0.78 miles of overhead hardening completed to date • 18 customers have benefitted from backup resiliency programs • Customers have been invited to participate in the Fixed Backup Program with a 36% adoption rate; additional customers will be invited in 2022
|  | Dec 2-4, 2020 | 144
|  | Dec 7-8, 2020 | 133
157 | San Diego | Dec 2-4, 2020 | 1028 | • 34.26 miles of overhead hardening completed to date; 33 miles in scope for 2022/2023 • Added or replaced 8 SCADA sectionalizing devices • 97 customers have benefitted from backup resiliency programs
|  | Dec 7-9, 2020 | 614
|  | Dec 23-24, 2020 | 660
214 | San Diego | Jan 28-29, 2018 | 359 | • 1.36 miles of overhead hardening completed to date • Added or replaced 2 SCADA sectionalizing devices • 59 customers have benefitted from backup resiliency programs
|  | Oct 15, 2018 | 360
|  | Nov 12-14, 2018 | 360
|  | Dec 2-4, 2020 | 682
|  | Dec 7-9, 2020 | 682
|  | Dec 23-24, 2020 | 682
215 | San Diego | Dec 3-4, 2020 | 510 | • 1.30 miles of overhead hardening completed to date • Added or replaced 4 SCADA sectionalizing devices • 83 customers have benefitted from backup resiliency programs
|  | Dec 7-8, 2020 | 385
|  | Dec 24, 2020 | 385
220 | San Diego | Dec 2-4, 2020 | 324 | • 3.42 miles of undergrounding in scope for 2023 • 0.15 miles of overhead hardening completed to date • Santa Ysabel Microgrid in scope for 2022 • 22 customers have benefitted from backup resiliency programs
|  | Dec 7-9, 2020 | 324
|  | Dec 24, 2020 | 324
222 | San Diego | Dec 2-4, 2020 | 1355 | • 2.52 miles of undergrounding in scope for 2022; 7.7 miles in scope for 2023 • 21.17 miles of overhead hardening completed to date; 3.18 miles in scope for 2022/2023 • Added or replaced 3 SCADA sectionalizing devices • 115 customers have benefitted from backup resiliency programs • Customers have been invited to participate in the Fixed Backup Program with a 36% adoption rate; additional customers will be invited in 2022
|  | Dec 7-10, 2020 | 1302
|  | Dec 23-24, 2020 | 402
238 | San Diego | Oct 10-11, 2019 | 2 | • Two meters belonging to one customer on Cir 238 were cut over to Cir 222 in mid-2020
|  | Oct 24-26, 2019 | 2
|  | Oct 29-Nov 1, 2019 | 2
|  | Nov 17, 2019 | 2
358 | San Diego | Dec 2-4, 2020 | 359 | • 1.62 miles of undergrounding in scope for 2022; 1.85 miles in scope for 2023 • 0.11 miles of overhead hardening completed to date • 48 customers have benefitted from backup resiliency programs
|  | Dec 7-8, 2020 | 247
|  | Dec 23-24, 2020 | 359
441 | San Diego | Oct 27, 2020 | 104 | • 4.9 miles of undergrounding in scope for 2023 • 0.19 miles of overhead hardening in scope for 2022 • Added or replaced 1 SCADA sectionalizing device • 10 customers have benefitted from backup resiliency programs • Customers have been invited to participate in the Fixed Backup Program with a 36% adoption rate; additional customers will be invited in 2022
|  | Dec 2-3, 2020 | 104
|  | Dec 7-8, 2020 | 104
445 | San Diego | Oct 10-11, 2019 | 344 | • 3.08 miles of undergrounding in scope for 2022; 43.21 miles in scope for 2023/2024 • 17.27 miles of overhead hardening completed to date; 16.68 miles in scope for 2022/2024 • Added or replaced 3 SCADA sectionalizing devices • 86 customers have benefitted from backup resiliency programs
|  | Oct 24-26, 2019 | 344
|  | Oct 30-31, 2019 | 344
|  | Oct 27, 2020 | 801
|  | Dec 2-4, 2020 | 967
|  | Dec 7-9, 2020 | 967
75 | San Diego | Dec 2-4, 2020 | 752 | • 6.83 miles of undergrounding completed to date; 4.16 miles in scope for 2022 • 47 customers have benefitted from backup resiliency programs
|  | Dec 7-9, 2020 | 16
|  | Dec 23-24, 2020 | 16
78 | San Diego | Dec 2-4, 2020 | 276 | • 0.35 miles of overhead hardening completed to date; 1.51 miles in scope for 2022 • Added or replaced 3 SCADA sectionalizing devices • 23 customers have benefitted from backup resiliency programs
|  | Dec 7-8, 2020 | 121
|  | Dec 24, 2020 | 276
79 | San Diego | Jan 27-29, 2018 | 838 | • 3.38 miles of undergrounding completed to date • 22.23 miles of overhead hardening completed to date; 4.65 miles in scope for 2022/2023 • Added or replaced 6 SCADA sectionalizing devices • 110 customers have benefitted from backup resiliency programs • Customers have been invited to participate in the Fixed Backup Program with a 36% adoption rate; additional customers will be invited in 2022
|  | Oct 15-16, 2018 | 20
|  | Oct 19-20, 2018 | 20
|  | Nov 11-15, 2018 | 852
|  | Oct 10-11, 2019 | 19
|  | Oct 24-26, 2019 | 870
|  | Oct 29-31, 2019 | 867
|  | Nov 17-18, 2019 | 19
|  | Sept 8-9, 2020 | 19
|  | Dec 2-4, 2020 | 879
|  | Dec 7-9, 2020 | 879
|  | Dec 23-24, 2020 | 18
909 | San Diego | Dec 2-4, 2020 | 494 | • Added or replaced 1 SCADA sectionalizing devices • 43 customers have benefitted from backup resiliency programs
|  | Dec 7-8, 2020 | 362
|  | Dec 23-24, 2020 | 494
CTL1 | San Diego | Dec 2-4, 2020 | 201 | • 26 customers have benefitted from backup resiliency programs
|  | Dec 7-9, 2020 | 201
|  | Dec 24, 2020 | 200

## MGRA 40a
Circuit | Date | Time | Type of Damage Submission | lat | long | asset damage height ft | asset category | asset category comment | voltage kv | pole or tower material | material comment | asset type | asset comment | likely arcing | damage category | damage category comment | damage desc
220 | 2020_12_04 | 13:00 | PSPS Circuit Patrol | 33.1354 | -116.6817 | 45 | Distribution Line | Customer reported tree on conductor | 12 kV | Wood | Customer reported tree on conductor | Conductor, OH | Customer reported tree on conductor | Yes | Extreme Wind | Customer reported tree on conductor | Customer reported tree on conductor
358 | 2020_12_04 | 10:35 | PSPS Circuit Patrol | 32.837 | -116.6917 | 45 | Other - See Comment | Loose Telco Lashing | 12 kV | Wood | NA | Other - See Comment | Loose Telco Lashing | No | Damaged Equipment | NA | 1235-A5
Loose Telco Lashing
AT&T on their way to Potrero for another damage and will swing by tonight and will fix their telco.
358 | 2020_12_04 | 10:45 | PSPS Circuit Patrol | 32.8378 | -116.6872 | 35 | Other - See Comment | Bad Service at 5945 Alpine Blv. due to tree | 12 kV | Wood | NA | Conductor, OH | Service Wire | No | Tree/Vegetation Contact | Tree Contact | TB-1235-B5
Bad Service at 5945 Alpine Blvd. due to tree
358 | 2020_12_08 | 11:30 | PSPS Circuit Patrol | 32.8516 | -116.6839 | 60 | Distribution Line | Tree contact. 1/0 aerial cable | 12 kV | Steel |  | Conductor, OH |  | No | Tree/Vegetation Contact | Tree contact. | 1235-B3 Tree contact. 1/0 aerial cable
1030 | 2020_12_08 | 14:30 | PSPS Circuit Patrol | 33.218 | -116.9253 | 48 | Pole or Tower | Wire on crossarm | 12 kV | Wood | NA | Pole | NA | Yes | Damaged Equipment | Wire on crossarm | Wire on crossarm.
1030 | 2020_12_24 | 8:21 | PSPS Circuit Patrol | 33.226 | -166.9235 | 45 | Pole or Tower | Wire popped off the insulator | 12 kV | Wood | Wire popped off the insulator | Insulator / Pin | Wire popped off the insulator | No | Undetermined | Wire popped off the insulator | Wire popped off the insulator
1030 | 2020_12_24 | 9:23 | PSPS Circuit Patrol | 33.2233 | -166.9235 | 50 | Pole or Tower | Brace Bolt fell out causing the line arm to lean over and go phase to phase on the buck | 12 kV | Wood | Brace Bolt fell out causing the line arm to lean over and go phase to phase on the buck | Wire Slap | Brace Bolt fell out causing the line arm to lean over and go phase to phase on the buck | No | Extreme Wind | Brace Bolt fell out causing the line arm to lean over and go phase to phase on the buck | Brace Bolt fell out causing the line arm to lean over and go phase to phase on the buck, in between P100231 and P100230.

## MGRA 40b
ID of Circuit | County | Dates of Outages | # of Customers Affected | Start Date/Time | End Date/Time | Duration (Min) | Customer-Days
1030 | San Diego | Oct 10-11, 2019 | 30 | 2019-10-10 20:26 | 2019-10-11 14:58 | 1112 | 33360
|  | Oct 24-25, 2019 | 185 | 2019-10-24 20:22 | 2019-10-25 18:05 | 1303 | 241055
|  | Oct 30-31, 2019 | 1341 | 2019-10-30 02:50 | 2019-10-31 13:22 | 2072 | 2778552
|  | Sept 9, 2020 | 30 | 2020-09-09 04:10 | 2020-09-09 07:34 | 204 | 6120
|  | Dec 2-4, 2020 | 1182 | 2020-12-02 18:25 | 2020-12-04 18:31 | 2886 | 3411252
|  | Dec 7-9, 2020 | 1363 | 2020-12-07 11:00 | 2020-12-09 09:09 | 2769 | 3774147
|  | Dec 23-24, 2020 | 30 | 2020-12-23 15:20 | 2020-12-24 10:01 | 1121 | 33630
1166 | San Diego | Dec 2-4, 2020 | 322 | 2020-12-02 20:15 | 2020-12-04 14:45 | 2550 | 821100
|  | Dec 7-8, 2020 | 60 | 2020-12-07 18:48 | 2020-12-08 09:21 | 873 | 52380
|  | Dec 23-24, 2020 | 322 | 2020-12-23 21:51 | 2020-12-24 12:05 | 854 | 274988
1215 | San Diego | Oct 27, 2020 | 133 | 2020-10-27 09:12 | 2020-10-27 16:17 | 425 | 56525
|  | Dec 2-4, 2020 | 144 | 2020-12-02 19:29 | 2020-12-04 13:55 | 2546 | 366624
|  | Dec 7-8, 2020 | 133 | 2020-12-07 20:33 | 2020-12-08 16:11 | 1178 | 156674
157 | San Diego | Dec 2-4, 2020 | 1028 | 2020-12-02 19:19 | 2020-12-04 14:48 | 2609 | 2682052
|  | Dec 7-9, 2020 | 614 | 2020-12-07 18:57 | 2020-12-09 10:54 | 2397 | 1471758
|  | Dec 23-24, 2020 | 660 | 2020-12-23 15:55 | 2020-12-24 14:55 | 1380 | 910800
214 | San Diego | Jan 28-29, 2018 | 359 | 2018-01-28 09:02 | 2018-01-29 15:48 | 1846 | 662714
|  | Oct 15, 2018 | 360 | 2018-10-15 10:28 | 2018-10-15 17:33 | 425 | 153000
|  | Nov 12-14, 2018 | 360 | 2018-11-12 07:51 | 2018-11-14 13:59 | 3248 | 1169280
|  | Dec 2-4, 2020 | 682 | 2020-12-02 19:49 | 2020-12-04 16:49 | 2700 | 1841400
|  | Dec 7-9, 2020 | 682 | 2020-12-07 16:51 | 2020-12-09 09:04 | 2413 | 1645666
|  | Dec 23-24, 2020 | 682 | 2020-12-24 02:07 | 2020-12-24 14:23 | 736 | 501952
215 | San Diego | Dec 3-4, 2020 | 510 | 2020-12-03 05:29 | 2020-12-04 17:45 | 2176 | 1109760
|  | Dec 7-8, 2020 | 385 | 2020-12-07 16:44 | 2020-12-08 12:56 | 1212 | 466620
|  | Dec 24, 2020 | 385 | 2020-12-24 01:04 | 2020-12-24 11:32 | 628 | 241780
220 | San Diego | Dec 2-4, 2020 | 324 | 2020-12-02 19:00 | 2020-12-04 21:24 | 3024 | 979776
|  | Dec 7-9, 2020 | 324 | 2020-12-07 13:38 | 2020-12-09 10:05 | 2667 | 864108
|  | Dec 24, 2020 | 324 | 2020-12-24 00:01 | 2020-12-24 13:07 | 786 | 254664
222 | San Diego | Dec 2-4, 2020 | 1355 | 2020-12-02 19:35 | 2020-12-04 19:12 | 2857 | 3871235
|  | Dec 7-10, 2020 | 1302 | 2020-12-07 15:30 | 2020-12-10 00:51 | 3441 | 4480182
|  | Dec 23-24, 2020 | 402 | 2020-12-23 23:27 | 2020-12-24 11:17 | 710 | 285420
238 | San Diego | Oct 10-11, 2019 | 2 | 2019-10-10 18:25 | 2019-10-11 15:34 | 1269 | 2538
|  | Oct 24-26, 2019 | 2 | 2019-10-24 04:09 | 2019-10-26 14:24 | 3495 | 6990
|  | Oct 29-Nov 1, 2019 | 2 | 2019-10-29 23:17 | 2019-11-01 08:53 | 3456 | 6912
|  | Nov 17, 2019 | 2 | 2019-11-17 05:07 | 2019-11-17 15:53 | 646 | 1292
358 | San Diego | Dec 2-4, 2020 | 359 | 2020-12-02 18:24 | 2020-12-04 13:45 | 2601 | 933759
|  | Dec 7-8, 2020 | 247 | 2020-12-07 17:49 | 2020-12-08 13:42 | 1193 | 294671
|  | Dec 23-24, 2020 | 359 | 2020-12-23 23:49 | 2020-12-24 09:40 | 591 | 212169
441 | San Diego | Oct 27, 2020 | 104 | 2020-10-27 09:12 | 2020-10-27 16:58 | 466 | 48464
|  | Dec 2-3, 2020 | 104 | 2020-12-02 18:44 | 2020-12-03 20:10 | 1526 | 158704
|  | Dec 7-8, 2020 | 104 | 2020-12-07 17:36 | 2020-12-08 17:05 | 1409 | 146536
445 | San Diego | Oct 10-11, 2019 | 344 | 2019-10-10 20:57 | 2019-10-11 17:28 | 1231 | 423464
|  | Oct 24-26, 2019 | 344 | 2019-10-24 09:14 | 2019-10-26 10:16 | 2942 | 1012048
|  | Oct 30-31, 2019 | 344 | 2019-10-30 01:53 | 2019-10-31 17:12 | 2359 | 811496
|  | Oct 27, 2020 | 801 | 2020-10-27 09:48 | 2020-10-27 16:24 | 396 | 317196
|  | Dec 2-4, 2020 | 967 | 2020-12-02 19:30 | 2020-12-04 14:03 | 2553 | 2468751
|  | Dec 7-9, 2020 | 967 | 2020-12-07 20:38 | 2020-12-08 17:28 | 1250 | 1208750
75 | San Diego | Dec 2-4, 2020 | 752 | 2020-12-02 20:25 | 2020-12-04 11:36 | 2351 | 1767952
|  | Dec 7-9, 2020 | 16 | 2020-12-07 13:29 | 2020-12-09 08:32 | 2583 | 41328
|  | Dec 23-24, 2020 | 16 | 2020-12-23 23:29 | 2020-12-24 14:22 | 893 | 14288
78 | San Diego | Dec 2-4, 2020 | 276 | 2020-12-02 21:00 | 2020-12-04 15:37 | 2557 | 705732
|  | Dec 7-8, 2020 | 121 | 2020-12-07 20:40 | 2020-12-08 15:20 | 1120 | 135520
|  | Dec 24, 2020 | 276 | 2020-12-24 00:51 | 2020-12-24 09:04 | 493 | 136068
79 | San Diego | Jan 27-29, 2018 | 838 | 2018-01-27 19:06 | 2018-01-29 12:53 | 2507 | 2100866
|  | Oct 15-16, 2018 | 20 | 2018-10-15 21:47 | 2018-10-16 09:09 | 682 | 13640
|  | Oct 19-20, 2018 | 20 | 2018-10-19 03:06 | 2018-10-20 09:38 | 1832 | 36640
|  | Nov 11-15, 2018 | 852 | 2018-11-11 20:45 | 2018-11-15 12:46 | 5281 | 4499412
|  | Oct 10-11, 2019 | 19 | 2019-10-10 18:24 | 2019-10-11 18:07 | 1423 | 27037
|  | Oct 24-26, 2019 | 870 | 2019-10-24 04:07 | 2019-10-26 13:29 | 3442 | 2994540
|  | Oct 29-31, 2019 | 867 | 2019-10-29 23:21 | 2019-10-31 16:41 | 2480 | 2150160
|  | Nov 17-18, 2019 | 19 | 2019-11-17 05:01 | 2019-11-18 08:42 | 1661 | 31559
|  | Sept 8-9, 2020 | 19 | 2020-09-08 20:57 | 2020-09-09 10:26 | 809 | 15371
|  | Dec 2-4, 2020 | 879 | 2020-12-02 17:42 | 2020-12-04 16:10 | 2788 | 2450652
|  | Dec 7-9, 2020 | 879 | 2020-12-07 13:05 | 2020-12-09 12:14 | 2829 | 2486691
|  | Dec 23-24, 2020 | 18 | 2020-12-23 15:12 | 2020-12-24 09:49 | 1117 | 20106
909 | San Diego | Dec 2-4, 2020 | 494 | 2020-12-02 23:27 | 2020-12-04 15:55 | 2428 | 1199432
|  | Dec 7-8, 2020 | 362 | 2020-12-07 15:23 | 2020-12-08 13:13 | 1310 | 474220
|  | Dec 23-24, 2020 | 494 | 2020-12-23 23:07 | 2020-12-24 10:22 | 675 | 333450
CTL1 | San Diego | Dec 2-4, 2020 | 201 | 2020-12-02 19:57 | 2020-12-04 19:52 | 2875 | 577875
|  | Dec 7-9, 2020 | 201 | 2020-12-07 16:57 | 2020-12-09 09:04 | 2407 | 483807
|  | Dec 24, 2020 | 200 | 2020-12-24 02:07 | 2020-12-24 14:23 | 736 | 147200

## MGRA 40c
ID of Circuit | Total Circuit Miles
1030 | 107.7
1166 | 24.3
1215 | 23.6
157 | 114.8
214 | 65.2
215 | 30.4
220 | 54.2
222 | 132.2
238* | 0
358 | 31.4
441 | 30.6
445 | 108.2
75 | 33.7
78 | 15
79 | 80.6
*Circuit 238 was cutover to circuit 222 in mid-2020